## Master Datas
Concealed PVC Pipe
Data
24-25-RSD 1.4.1(b) |  | Replacement of old u/s with new Supply and laying of ISI 25mm outer dia medium grade with IS:9537 part 3 rigidPVC pipe concealed in wall with PVC / Metallic junction boxes, accessories including masonary work for light, fan and separate plug point including chisseling brick work, engaging skilled mason for fine wall cement plastering & all labour charges etc., complete for Modular concealed wiring. Makes : Sudhakar/Modi
|  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 775 | 1550
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
| 4 | Mason Cl- I / Brick layer Cl- I SOR-2025-26 Sl No 11 of skilled Labour rates. | 2 | day | 1 | day | 680 | 1360
|  | Labour Rate Per 100 Rm | [5 empty] | 5510
|  | Labour Rate for 1 Mtr | [5 empty] | 55.1
|  | Add GHMC allowance@40% | [5 empty] | 22.04
|  | Labour Sub total | [5 empty] | 77.14
b) Material
ELEC-10.4.10 | 5 | Cement (ELEC-10.4.10) | 50 | Kg | 1 | Kg | 9 | 450
ELEC-10.1.4 | 6 | U Nails (ELEC-10.1.4) | 200 | Nos | 100 | Nos | 44 | 88
ELEC-1.2.6 b | 7 | Supply of 25 mm PVC Junction Boxes Normal Makes: Sudhakar/Modi | 12 | Nos | 1 | Nos | 29 | 348
ELEC-1.2.8 b | 8 | Supply of 25mm dia medium grade PVC Bends makes: Sudhakar/Modi | 12 | Nos | 1 | No | 13 | 156
ELEC-1.2.2 b | 9 | Supply of ISI 25mm outer dia medium grade with IS:9537 part 3 regid PVC pipe of makes Sudhakar/Modi | 100 | Mtr | 1 | Mtr | 34 | 3400
|  | Material Rate for 100 Mtrs | [5 empty] | 4442
|  | Material Rate for 1 Mtr | [5 empty] | 44.42
|  | Total Cost of Material + Labour Charges | [5 empty] | 121.56
|  | Add Overhead @ 10.615% | [5 empty] | 12.9036
|  | Total Rate | [5 empty] | 134.4636
|  | Rounded off rate | [5 empty] | 134
Surface PVC Pipe
Data
24-25 RSD 1.3.2 |  | Replacement of old u/s with new Supply and Fixing of ISI marked 25mm outer dia medium grade with IS:9537 part 3 regid PVC pipe on surface of wall with PVC / Metallic junction boxes fixing on chromium plated metallic base saddles including all required materials with redoing wall fine cement plastering etc., completewith all labour charges for run of mains.(Data No.24-25 SD-1.3.2)
Makes :Sudhakar/Modi
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 775 | 1550
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
|  | Labour Rate Per 100 Rm | [5 empty] | 4150
|  | Labour Rate for 1 Mtr | [5 empty] | 41.5
|  | Add GHMC Allowance @40% | [5 empty] | 16.6
|  | Labour subtotal | [5 empty] | 58.1
b) Material
Elec 10.1.2 | 4 | Rawl Plugs. (SOR-2025-26- ELEC-10.1.2) | 200 | Nos | 100 | Nos | 45 | 90
Elec 1.4.4-d | 5 | Supply of No.8 Screws of 35/38mm. (SOR-2025-26 ELEC-1.4.4-d) | 200 | Nos | 100 | Nos | 142 | 284
Elec 10.4.10 | 6 | Cement. ( SOR 24-25 ELEC-10.4.10 ) | 5 | Kg | 1 | Kg | 9 | 45
ELEC-1.1.11 b | 7 | Supply of 25mm Saddles with Base. (SOR-2025-26-ELEC-1.1.11-b) | 200 | Nos | 100 | Nos | 319 | 638
ELEC-1.2.6 b | 8 | Supply of 25 mm PVC Junction Boxes NormalMakes: Sudhakar/Modi | 12 | Nos | 1 | No | 29 | 348
ELEC-1.2.8 b | 9 | Supply of 25mm dia medium grade PVC Bends makes: Sudhakar/Modi | 12 | Nos | 1 | No | 13 | 156
Elec 1.2.2 b | 10 | Supply of ISI 25mm outer dia medium grade with IS:9537 part 3 regid PVC pipe of makes Sudhakar/Modi | 100 | Mtr | 1 | Mtr | 34 | 3400
|  | Material Rate for 100 Mtrs | [5 empty] | 4961
|  | Material Rate for 1 Mtr | [5 empty] | 49.61
|  | Total Cost of Material + Labour Charges | [5 empty] | 107.71
|  | Add Overhead @ 10.615% | [5 empty] | 11.4334
|  | Total Rate | [5 empty] | 119.1434
|  | Rounded off rate | [5 empty] | 119
Light & Bell Points : Residential Building
Data
24-25-RSD 2.1.2 | 24-25-RSD2.1.2 | Rewiring with run of 2 of 1.5Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable in existing consealed pipe including supply and fixing of 3 Plate Jumbo Ceiling rose of Makes : GM G Home / Gold Medal Olive / Million Zoom make ,10A ISI marked Modular type switch with cover frame and necessary modular box duly concealed in wall including cost and conveyance of all material and all labour charges etc., complete for light and bell points in R.B. Copper cable Makes :Finolex / RR kabel / Havells / Polycab Switch Makes :Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.7 | day | 1 | day | 775 | 542.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1.4 | day | 1 | day | 650 | 910
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.7 | day | 1 | day | 650 | 455
|  | Labour Rate Per 7 pts | [5 empty] | 1907.5
|  | Labour Rate for 1 pt | [5 empty] | 272.5
|  | Add GHMC allowance @40% | [5 empty] | 109
|  | Labour Sub total | [5 empty] | 381.5
b) Material
ELEC-1.5.1-a | 4 | Supply of 1.5Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 100 | Mtrs | 100 | Mtr | 2530 | 2530
ELEC-1.7.1.m | 5 | Supply of 3 Plate Jumbo Ceiling Rose of Makes : GM G Home / Gold Medal Olive / Million Zoom | 7 | Nos | 1 | No | 25 | 175
ELEC-1.3.1.b | 6 | Supply of 3 Module box. | 1 | Nos | 1 | No | 116 | 116
ELEC-1.3.1.c | 7 | Supply of 4 Module box. | 1 | Nos | 1 | No | 137 | 137
ELEC-1.3.4.b | 8 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 95 | 95
ELEC-1.3.4.c | 9 | Supply of 4 Modular Cover Frame of makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 110 | 110
ELEC-1.9.2.a | 10 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 7 | Nos | 1 | No | 89 | 623
|  | Total material cost for 7 pts | [5 empty] | 3786
|  | Total material cost for 1 pt | [5 empty] | 540.8571
|  | Total Material and Labour charges for 1 pt | [5 empty] | 922.3571
|  | Add Overhead @ 10.615% | [5 empty] | 97.9082
|  | Sub Total Rate | [5 empty] | 1020.2654
Elec 1.5.4 |  | Deduction of finalised item cost acc. to NOTE 2 : If FRLSH (FRLS) Wires are used instead of HFFR during execution of work, for arrig the FRLSH (FRLS) Flexible wires rates 15% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains.NOTE 3 : If Class - II conductor Wires are not used 5% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains. | [5 empty] | 816.2123
|  | Rounded off rate | [5 empty] | 816
Light & Bell Points : Non-Residential Building
Data
24-25-RSD 2.1.2 | 24-25-RSD2.1.2 | Rewiring with run of 2 of 1.5Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable in existing consealed pipe including supply and fixing of 3 Plate Jumbo Ceiling rose of Makes : GM G Home / Gold Medal Olive / Million Zoom make ,10A ISI marked Modular type switch with cover frame and necessary modular box duly concealed in wall including cost and conveyance of all material and all labour charges etc., complete for light and bell points in R.B. Copper cable Makes :Finolex / RR kabel / Havells / Polycab Switch Makes :Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.7 | day | 1 | day | 775 | 542.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1.4 | day | 1 | day | 650 | 910
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.7 | day | 1 | day | 650 | 455
|  | Labour Rate Per 6 pts | [5 empty] | 1907.5
|  | Labour Rate for 1 pt | [5 empty] | 272.5
|  | Add GHMC allowance @40% | [5 empty] | 109
|  | Labour Sub total | [5 empty] | 381.5
b) Material
ELEC-1.5.1-a | 4 | Supply of 1.5Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 100 | Mtrs | 100 | Mtr | 2530 | 2530
ELEC-1.7.1.m | 5 | Supply of 3 Plate Jumbo Ceiling Rose of Makes : GM G Home / Gold Medal Olive / Million Zoom | 6 | Nos | 1 | No | 25 | 150
ELEC-1.3.1.b | 6 | Supply of 3 Module box. | 1 | Nos | 1 | No | 116 | 116
ELEC-1.3.1.c | 7 | Supply of 4 Module box. | 1 | Nos | 1 | No | 137 | 137
ELEC-1.3.4.b | 8 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 95 | 95
ELEC-1.3.4.c | 9 | Supply of 4 Modular Cover Frame of makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 110 | 110
ELEC-1.9.2.a | 10 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 6 | Nos | 1 | No | 89 | 534
|  | Total material cost for 6 pts | [5 empty] | 3672
|  | Total material cost for 1 pt | [5 empty] | 612
|  | Total Material and Labour charges for 1 pt | [5 empty] | 993.5
|  | Add Overhead @ 10.615% | [5 empty] | 105.46
|  | Sub Total Rate | [5 empty] | 1098.96
Elec 1.5.4 |  | Deduction of finalised item cost acc. to NOTE 2 : If FRLSH (FRLS) Wires are used instead of HFFR during execution of work, for arrig the FRLSH (FRLS) Flexible wires rates 15% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains.NOTE 3 : If Class - II conductor Wires are not used 5% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains. | [5 empty] | 879.168
|  | Rounded off rate | [5 empty] | 879
Fan and Exhaust Fan Points : Residential Building
Data
24-25-RSD 2.1.2 |  | Rewiring with 3 runs of 1.5Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable in existing consealed pipe including supply and fixing of 3 Plate Jumbo Ceiling rose of GM G Home / Gold Medal Olive / Million Zoommake , 10A ISI marked Modular type switch with cover frame and necessary modular box duly concealed in wall including cost and conveyance of all material and all labour charges etc., complete for fan and exhaust fan points in Residential Buildings of Copper cable Makes : Finolex / RR kabel / Havells / Polycab Switch Makes :Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.7 | day | 1 | day | 775 | 542.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1.4 | day | 1 | day | 650 | 910
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.7 | day | 1 | day | 650 | 455
|  | Labour Rate Per 7 pts | [5 empty] | 1907.5
|  | Labour Rate for 1 pt | [5 empty] | 272.5
|  | Add GHMC allowance @40% | [5 empty] | 109
|  | Labour Sub total | [5 empty] | 381.5
b) Material
ELEC-1.5.1-a | 4 | Supply of 1.5 Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 150 | Mtrs | 100 | Mtr | 2530 | 3795
ELEC-1.7.1.m | 5 | Supply of 3 Plate Jumbo Ceiling Rose of Makes : GM G Home / Gold Medal Olive / Million Zoom | 7 | Nos | 1 | No | 25 | 175
ELEC-1.3.1.b | 6 | Supply of 3 Module box. | 1 | Nos | 1 | No | 116 | 116
ELEC-1.3.1.c | 7 | Supply of 4 Module box. | 1 | Nos | 1 | No | 137 | 137
ELEC-1.3.4.b | 8 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 95 | 95
ELEC-1.3.4.c | 9 | Supply of 4 Modular Cover Frame of makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 110 | 110
ELEC-1.9.2.a | 10 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 7 | Nos | 1 | No | 89 | 623
|  | Total material cost for 7 pts | [5 empty] | 5051
|  | Total material cost for 1 pt | [5 empty] | 721.5714
|  | Total Material and Labour charges for 1 pt | [5 empty] | 1103.0714
|  | Add Overhead @ 10.615% | [5 empty] | 117.091
|  | Total Rate | [5 empty] | 1220.1625
Elec 1.5.4 |  | Deduction of finalised item cost acc. to NOTE 2 : If FRLSH (FRLS) Wires are used instead of HFFR during execution of work, for arrig the FRLSH (FRLS) Flexible wires rates 15% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains.NOTE 3 : If Class - II conductor Wires are not used 5% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains. | [5 empty] | 976.13
|  | Rounded off rate | [5 empty] | 976
Fan and Exhaust Fan Points : Non-Residential Building
Data
24-25-RSD 2.1.2 |  | Rewiring with 3 runs of 1.5Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable in existing consealed pipe including supply and fixing of 3 Plate Jumbo Ceiling rose of GM G Home / Gold Medal Olive / Million Zoommake , 10A ISI marked Modular type switch with cover frame and necessary modular box duly concealed in wall including cost and conveyance of all material and all labour charges etc., complete for fan and exhaust fan points in Residential Buildings of Copper cable Makes : Finolex / RR kabel / Havells / Polycab Switch Makes :Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.7 | day | 1 | day | 775 | 542.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1.4 | day | 1 | day | 650 | 910
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.7 | day | 1 | day | 650 | 455
|  | Labour Rate Per 7 pts | [5 empty] | 1907.5
|  | Labour Rate for 1 pt | [5 empty] | 272.5
|  | Add GHMC allowance @40% | [5 empty] | 109
|  | Labour Sub total | [5 empty] | 381.5
b) Material
ELEC-1.5.1-a | 4 | Supply of 1.5 Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 150 | Mtrs | 100 | Mtr | 2530 | 3795
ELEC-1.7.1.m | 5 | Supply of 3 Plate Jumbo Ceiling Rose of Makes : GM G Home / Gold Medal Olive / Million Zoom | 7 | Nos | 1 | No | 25 | 175
ELEC-1.3.1.b | 6 | Supply of 3 Module box. | 1 | Nos | 1 | No | 116 | 116
ELEC-1.3.1.c | 7 | Supply of 4 Module box. | 1 | Nos | 1 | No | 137 | 137
ELEC-1.3.4.b | 8 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 95 | 95
ELEC-1.3.4.c | 9 | Supply of 4 Modular Cover Frame of makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 110 | 110
ELEC-1.9.2.a | 10 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 7 | Nos | 1 | No | 89 | 623
|  | Total material cost for 7 pts | [5 empty] | 5051
|  | Total material cost for 1 pt | [5 empty] | 721.5714
|  | Total Material and Labour charges for 1 pt | [5 empty] | 1103.0714
|  | Add Overhead @ 10.615% | [5 empty] | 117.091
|  | Total Rate | [5 empty] | 1220.1625
Elec 1.5.4 |  | Deduction of finalised item cost acc. to NOTE 2 : If FRLSH (FRLS) Wires are used instead of HFFR during execution of work, for arrig the FRLSH (FRLS) Flexible wires rates 15% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains.NOTE 3 : If Class - II conductor Wires are not used 5% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains. | [5 empty] | 976.13
|  | Rounded off rate | [5 empty] | 976
Common Switch Board
Data
24-25 RSD 2.1.4 |  | Replacement of old u/s with new Supply and fixing of ISI Marked 10A 3/2 pin Modular socket with shutter with 10A 1way Modular switch and cover frame on a common switch board with Module box with connections including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.067 | day | 1 | day | 775 | 51.925
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.067 | day | 1 | day | 650 | 43.55
|  | Labour for 1 Point | [5 empty] | 95.475
|  | Add GHMC allowance @40% | [5 empty] | 38.19
|  | Labour Sub total | [5 empty] | 133.665
b) Material
ELEC-1.3.1.b | 3 | Supply of 3 Module box. | 1 | Nos | 1 | No | 116 | 116
ELEC-1.3.4.b | 4 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 95 | 95
ELEC-1.9.2.a | 5 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 89 | 89
ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 131 | 131
|  | Total material cost | [5 empty] | 431
|  | Total Material and Labour charges for 1 no | [5 empty] | 564.665
|  | Add Overhead @ 10.615% | [5 empty] | 59.9392
|  | Total Rate | [5 empty] | 624.6042
|  | Rounded off rate | [5 empty] | 625
Power Plug
Data
24-25 RSD 2.1.6 |  | Replacement of old u/s with new Supply and fixing of ISI marked 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter, 16 Amps Modular switch on a 3 Modular box with suitable cover frame with connections including cost and conveyance of all material and all labour charges etc., complete in N.R.B. / R.B. Makes Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.1 | day | 1 | day | 775 | 77.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 650 | 65
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 650 | 65
|  | Labour for 1 No | [5 empty] | 207.5
|  | Add GHMC allowance @40% | [5 empty] | 83
|  | Labour Sub total | [5 empty] | 290.5
b) Material
ELEC-1.3.1.b | 4 | Supply of 3 Module box. | 1 | Nos | 1 | No | 116 | 116
ELEC-1.3.4.b | 5 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 95 | 95
ELEC-1.9.2.h | 6 | Supply of 16A / 20A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 116 | 116
ELEC-1.9.2.L | 7 | Supply of 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 189 | 189
|  | Total material cost | [5 empty] | 516
|  | Total Material and Labour charges for 1 no | [5 empty] | 806.5
|  | Add Overhead @ 10.615% | [5 empty] | 85.61
|  | Total Rate | [5 empty] | 892.11
|  | Rounded off rate | [5 empty] | 892
Power Plug Two Nos
Data
24-25 RSD 2.1.6X2 |  | Replacement of old u/s with new Supply and fixing of 2 No.s ISI marked 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter, 16 Amps Modular switch on suitable Modular box with suitable cover frame with connections including cost and conveyance of all material and all labour charges etc., complete in N.R.B. / R.B. Makes :Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.2 | day | 1 | day | 775 | 155
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.2 | day | 1 | day | 650 | 130
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.2 | day | 1 | day | 650 | 130
|  | Labour for 1 No | [5 empty] | 415
|  | Add GHMC allowance @40% | [5 empty] | 166
|  | Labour Sub total | [5 empty] | 581
b) Material
ELEC-1.3.1.d | 4 | Supply of 6 Module box. | 1 | Nos | 1 | No | 189 | 189
ELEC-1.3.4.d | 5 | Supply of 6 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 150 | 150
ELEC-1.9.2.h | 6 | Supply of 16A / 20A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 2 | Nos | 1 | No | 116 | 232
ELEC-1.9.2.L | 7 | 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 2 | Nos | 1 | No | 189 | 378
|  | Total material cost | [5 empty] | 949
|  | Total Material and Labour charges for 1 no | [5 empty] | 1530
|  | Add Overhead @ 10.615% | [5 empty] | 162.4095
|  | Total Rate | [5 empty] | 1692.4095
|  | Rounded off rate | [5 empty] | 1692
6Module (6A Sockets & -6A Switches - Two Nos)
Data
24-25 RSD 2.1.4X2 |  | Replacement of old u/s with new Supply and fixing of 2 no.s ISI Marked 10A 3/2 pin Modular socket with shutter with 2 No.s 10A 1way Modular switch and cover frame on a common switch board with Module box with connections including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes :Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.134 | day | 1 | day | 775 | 103.85
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.134 | day | 1 | day | 650 | 87.1
|  | Labour for 1 Point | [5 empty] | 190.95
|  | Add GHMC allowance @40% | [5 empty] | 76.38
|  | Labour Sub total | [5 empty] | 267.33
b) Material
ELEC-1.3.1.d | 3 | Supply of 6 Module box. | 1 | Nos | 1 | No | 189 | 189
ELEC-1.3.4.d | 4 | Supply of 6 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 150 | 150
ELEC-1.9.2.a | 5 | Supply of 10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 2 | Nos | 1 | No | 89 | 178
ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 2 | Nos | 1 | No | 131 | 262
|  | Total material cost | [5 empty] | 779
|  | Total Material and Labour charges for 1 no | [5 empty] | 1046.33
|  | Add Overhead @ 10.615% | [5 empty] | 111.0679
|  | Total Rate | [5 empty] | 1157.3979
|  | Rounded off rate | [5 empty] | 1157
8Module (6A Sockets & -6A Switches - Three Nos)
Data
24-25 RSD 2.1.4X3 |  | Replacement of old u/s with new Supply and fixing of ISI marked 3 Nos 10A Modular type switches with 2 Nos 10A 3/2 pin Modular plug sockets with shutter on 8 Modular box with cover frame including connections, cost and coveyance of all material and all labour charges etc., complete for Computers in N.R.B. / R.B. Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.2 | day | 1 | day | 775 | 155
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.2 | day | 1 | day | 650 | 130
|  | Labour for 1 No | [5 empty] | 285
|  | Add GHMC allowance @40% | [5 empty] | 114
|  | Labour Sub total | [5 empty] | 399
b) Material
ELEC-1.3.1.e | 3 | Supply of 8/9 Horizontal/Vertical Module box. | 1 | Nos | 1 | No | 247 | 247
ELEC-1.3.4.e | 4 | Supply of 8 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 185 | 185
ELEC-1.9.2.a | 5 | Supply of 10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 2 | Nos | 1 | No | 89 | 178
ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 3 | Nos | 1 | No | 131 | 393
|  | Total material cost | [5 empty] | 1003
|  | Total Material and Labour charges for 1 no | [5 empty] | 1402
|  | Add Overhead @ 10.615% | [5 empty] | 148.8223
|  | Total Rate | [5 empty] | 1550.8223
|  | Rounded off rate | [5 empty] | 1551
12Module (6A Sockets & -6A Switches - Four Nos)
Data
24-25 RSD 2.1.4X4 |  | Replacement of old u/s with new Supply and fixing of ISI marked 4 Nos 10A Modular type switches with 4 Nos 10A 3/2 pin Modular plug sockets with shutter on 12 Modular box with cover frame including connections, cost and coveyance of all material and all labour charges etc., complete for Computers in N.R.B. / R.B. Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.25 | day | 1 | day | 775 | 193.75
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.25 | day | 1 | day | 650 | 162.5
|  | Labour for 1 No | [5 empty] | 356.25
|  | Add GHMC allowance @40% | [5 empty] | 142.5
|  | Labour Sub total | [5 empty] | 498.75
b) Material
ELEC-1.3.1.f | 3 | Supply of 12 Module box. | 1 | Nos | 1 | No | 299 | 299
ELEC-1.3.4.f | 4 | Supply of 12 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 230 | 230
ELEC-1.9.2.a | 5 | Supply of 10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 4 | Nos | 1 | No | 89 | 356
ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 4 | Nos | 1 | No | 131 | 524
|  | Total material cost | [5 empty] | 1409
|  | Total Material and Labour charges for 1 no | [5 empty] | 1907.75
|  | Add Overhead @ 10.615% | [5 empty] | 202.5077
|  | Total Rate | [5 empty] | 2110.2577
|  | Rounded off rate | [5 empty] | 2110
Ding Dong Bell
Data
24-25 RSD-2.1.13 |  | Replacement of old u/s with new Supply and fixing of Ding Dong Bell of makes GM / Million / Gold Medal / Anchor / Great white,in lieu of Ceiling rose, including giving connections, cost of all accessories and labour charges etc., complete.
Makes : GM / Million / Gold Medal /Anchor / Great White.
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.062 | No | 1 | No | 775 | 48.05
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.062 | day | 1 | day | 650 | 40.3
|  | Labour for 1 No | [5 empty] | 88.35
|  | Add GHMC Allowance @40% | [5 empty] | 35.34
|  | Labour subtotal | [5 empty] | 123.69
b) Material
ELEC-1.7.2 b | 3 | Supply of Ding Dong Bell of Makes :GM / Million / Gold Medal / Anchor / Great white. | 1 | Nos | 1 | No | 125 | 125
|  | Cost of Material | [5 empty] | 125
|  | Total Cost of Material + Labour Charges | [5 empty] | 248.69
|  | Add Overhead @ 10.615% | [5 empty] | 26.3984
|  | Total Rate | [5 empty] | 275.0884
|  | Rounded off rate | [5 empty] | 275
1200mm length LED light
Data
SD-N.A |  | Replacement of old u/s with newSupply and transportation of 22W +/ 10% , >/ 2300 lumens, 1200 mm (+/- 10%) length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<15%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 2 years warranty with BIS Certification with BIS Certification. LUMINAIRE MAKE : Phillips / Wipro / Crompton / Havells LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs. ,
a) Labour charges
|  | Labour for 1 No | [5 empty] | 30
|  | Add GHMC Allowance @40% | [5 empty] | 12
|  | Labour Sub total | [5 empty] | 42
b) Material
Cost of Material for fixing luminaire
ELEC-3.3.16 | 7 | Supply and transportation of 22W +/ 10% , >/ 2300 lumens, 1200 mm (+/- 10%) length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<15%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 5 years warranty with BIS Certification with BIS Certification. LUMINAIRE MAKE : Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Eveready / Surya / Keselec / Arraystorm / GM / Goldmedal / Goldwyn / Fortune Arrt / Lighting Technologies / Bee-Lite LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs. | 1 | No | 1 | No | 387.1 | 387.1
|  | Cost of Material | [5 empty] | 387.1
|  | Total Cost of Material + Labour Charges | [5 empty] | 429.1
|  | Add Overhead @ 10.615% | [5 empty] | 45.549
|  | Total Rate | [5 empty] | 474.649
|  | Rounded off rate | [5 empty] | 475
15W LED Slimline Panel Light
Data
SD-NA |  | Replacement of old u/s with new Supply and transportation of 15W +/-10% (>= 1350 Lumens)edge lit LED slimline panel light Housing made of Pressure die cast aluminium with Powder coated, round / Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE : Phillips / Wipro / Crompton / Havells LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs.
a) Labour charges
|  | Labour for 1 No | [5 empty] | 50
|  | Add GHMC Allowance @40% | [5 empty] | 20
|  | Labour Sub total | [5 empty] | 70
b) Material
ELEC- 3.3.7-c | 4 | Supply and transportation of 15W +/-10% (>= 1350 Lumens)edge lit LED slimline panel light Housing made of Pressure die cast aluminium with Powder coated, round / Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE : Phillips / Wipro / Crompton / Havells LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs. | 1 | no | 1 | no | 611.8 | 611.8
| 5 | Alluminium Flat,screws / hooks,binding wire (As per requirement). | [5 empty] | 20
|  | Cost of Material for fixing luminaire | [5 empty] | 631.8
|  | Total Cost of Material + Labour Charges | [5 empty] | 701.8
|  | Add Overhead @ 10.615% | [5 empty] | 74.4961
|  | Total Rate | [5 empty] | 776.2961
|  | Rounded off rate | [5 empty] | 776
15W LED Surface Mounted Down Light
Data
SD-NA |  | Replacement of old u/s with new Supply and transportation of 15 W +/-10% (>= 1500 Lumens) back lit LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE : Phillips / Wipro / Crompton / Bajaj / Havells LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs.
a) Labour charges
|  | Labour for 1 No | [5 empty] | 50
|  | Add GHMC Allowance @40% | [5 empty] | 20
|  | Labour Sub total | [5 empty] | 70
b) Material
ELEC- 3.3.4 b | 4 | Supply and transportation of 15 W +/-10% (>= 1500 Lumens) back lit LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE : Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Eveready / Surya / Keselec / Arraystorm / GM / Goldmedal / Goldwyn / Fortune Arrt / Lighting Technologies / Bee-Lite LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs. | 1 | no | 1 | no | 910 | 910
| 5 | Alluminium Flat,screws / hooks,binding wire (As per requirement). | [5 empty] | 20
|  | Cost of Material for fixing luminaire | [5 empty] | 930
|  | Total Cost of Material + Labour Charges | [5 empty] | 1000
|  | Add Overhead @ 10.615% | [5 empty] | 106.15
|  | Total Rate | [5 empty] | 1106.15
|  | Rounded off rate | [5 empty] | 1106
Ceiling Fans
Data
24-25 RSD 9.7.2+ RSD9.7.35 |  | Replacement of old u/s with new Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: F, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 8.6, Air delivery minimum 235 CMM, 350 RPM( tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75°C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete with 5 years warranty.Makes:Atomberg (Efficio ) / Havells / Orient / Crompton
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.125 | day | 1 | day | 775 | 96.875
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.125 | day | 1 | day | 650 | 81.25
|  | Deduct labour for not fixing Regulator | -0.1 | Nos | 1 | Nos | 650 | -65
|  | Labour for 1 No | [5 empty] | 113.125
|  | Add GHMC Allowance @40% | [5 empty] | 45.25
|  | Labour Sub total | [5 empty] | 158.375
b) Material
Elec- 1.5.4 | 3 | Supply of 23 / 0060 , 3 core (0.15 mm dia of each lead) twisted / flat heavy Copper wire. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Gemini / Vimal / Suncab / Pawancab | 1 | Mtr | 100 | Mtrs | 1390 | 13.9
Elec-5.1.2 | 4 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: F, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 8.6, Air delivery minimum 235 CMM, 350 RPM( tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75°C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete with 5 years warranty.Makes:Atomberg (Efficio ) / Havells / Bajaj / Orient / Halonix / Crompton/Goldmedal / GM. | 1 | Nos | 1 | Nos | 3085 | 3085
|  | Transportation of material |  |  |  |  | 1% | 30.85
|  | Cost of Material for 1 No | [5 empty] | 3129.75
|  | Total Cost of Material + Labour Charges | [5 empty] | 3288.125
|  | Add Overhead @ 10.615% | [5 empty] | 349.0345
|  | Total Rate | [5 empty] | 3637.1595
|  | Rounded off rate | [5 empty] | 3637
Stepped Electronic Regulator
Data
24-25 RSD 9.7.26 |  | Replacement of old u/s with new Supply and fixing of Modular type Stepped electronic regulator with connections and Labour charges etc complete. Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges
| 1 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | Nos | 1 | Nos | 650 | 65
|  | Labour for 1 No | [5 empty] | 65
|  | Add GHMC Allowance @40% | [5 empty] | 26
|  | Labour Sub total | [5 empty] | 91
b) Material
ELEC-1.9.2.n | 2 | Supply of 2 Module Modular type Electronic Fan Regulator of Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | Nos | 525 | 525
|  | Total material cost | [5 empty] | 525
|  | Total Cost of Material + Labour Charges | [5 empty] | 616
|  | Add Overhead @ 10.615% | [5 empty] | 65.3884
|  | Total Rate | [5 empty] | 681.3884
|  | Rounded off rate | [5 empty] | 681
4Module 3W LED Foot lamp
Data
24-25 RSD 8.1.1 |  | Replacement of old u/s with new Supply ,Transportation and fixing of 4Module 3W LED Foot lamp as desired by the department and as per IS,inlcuding all labour charges etc., complete of make GM Four Five.
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.04 | day | 1 | day | 775 | 31
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.04 | day | 1 | day | 650 | 26
|  | Labour | [5 empty] | 57
|  | Add GHMC Allowance @40% | [5 empty] | 22.8
|  | Labour subtotal | [5 empty] | 79.8
b) Material
| 3 | Supply ,Transportation of 4Module 3W LED Foot lamp of make GM Four Five(Approved rate from MRC Qtrs) | 1 | No | 1 | No | 545 | 545
|  | Cost of Material | [5 empty] | 545
|  | Total Cost of Material + Labour Charges | [5 empty] | 624.8
|  | Rounded of Rate | [5 empty] | 625
Mirror Lights
Data
SD-N.A |  | Replacement of old u/s with new Supply and transportation of 10W, 1000 lumens, 600 mm (+/- 10%) length LED batten tube light, housing made with PC body, wide operating voltage with Single / double side connection, PF≥0.9, Surge protection: > 2KV, THD<15%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department and as per IS specifications, minimum CRI≥80,.etc complete with 5 years warranty with BIS Certification.LUMINAIRE MAKE : Phillips / Wipro / Crompton / Havells LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs.
a) Labour charges
|  | Labour for 1 No | [5 empty] | 30
|  | Add GHMC Allowance @40% | [5 empty] | 12
|  | Labour Sub total | [5 empty] | 42
b) Material
Cost of Material for fixing luminaire
ELEC-3.3.15 | 7 | Supply and transportation of 10W, 1000 lumens, 600 mm (+/- 10%) length LED batten tube light, housing made with PC body, wide operating voltage with Single / double side connection, PF≥0.9, Surge protection: > 2KV, THD<15%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department and as per IS specifications, minimum CRI≥80,.etc complete with 5 years warranty with BIS Certification.LUMINAIRE MAKE : PPhillips / Wipro / Crompton / Havells LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs. | 1 | No | 1 | No | 242.2 | 242.2
|  | Cost of Material | [5 empty] | 242.2
|  | Total Cost of Material + Labour Charges | [5 empty] | 284.2
|  | Add Overhead @ 10.615% | [5 empty] | 30.1678
|  | Total Rate | [5 empty] | 314.3678
|  | Rounded off rate | [5 empty] | 314
Exhaust Fan
Data
24-25 RSD 9.7.2+RSD 9.7.36 |  | Replacement of old u/s with new Supply of 12" (300mm +/ - 5%)Light duty exhaust fan with metal blades etc complete for ante rooms / individual toilets. Makes : Crompton / Havells VentilairDSP / Orient hill air.
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.25 | day | 1 | day | 775 | 193.75
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.25 | day | 1 | day | 650 | 162.5
|  | Labour for 1 No | [5 empty] | 356.25
|  | Add GHMC Allowance @40% | [5 empty] | 142.5
|  | Labour subtotal | [5 empty] | 498.75
| 3 | Sundries such as Bolt, Nuts, twin core wire if necessary etc. |  |  |  |  | 15 | 15
|  | Cost of Material for fixing fan | [5 empty] | 15
b) Material
ELEC-5.1.11 b | 4 | Supply of 12" (300mm +/ - 5%)Light duty exhaust fan with metal blades etc complete for ante rooms / individual toilets. Makes : Crompton / Havells VentilairDSP / Orient hill air. | 1 | No | 1 | No | 1817 | 1817
|  | Transportation Charges on Unit Cost @1% |  |  |  |  | 1% | 18.17
|  | Cost of Material for 1 No | [5 empty] | 1850.17
|  | Total Cost of Material + Labour Charges | [5 empty] | 2348.92
|  | Add Overhead @ 10.615% | [5 empty] | 249.3379
|  | Total Rate | [5 empty] | 2598.2579
|  | Rounded off rate | [5 empty] | 2598
Run of 3 of 2.5 Sq.mm Copper Cable
Data
24-25 RSD 3.1.4 |  | Rewiring with Supply and Run of 3 of 2.5 Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable in existing pipe for run of mains inlcuding all labour charges etc., complete Copper cable Makes :Finolex / RR kabel / Havells / Polycab
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.67 | day | 1 | day | 775 | 519.25
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.67 | day | 1 | day | 650 | 435.5
|  | Labour for 100 Mtr | [5 empty] | 2254.75
|  | Labour for 1 Mtr | [5 empty] | 22.5475
|  | Add GHMC Allowance @40% | [5 empty] | 9.019
|  | Labour subtotal | [5 empty] | 31.5665
b) Material
ELEC-1.5.1-b | 4 | Supply of 2.5 Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 300 | Mtrs | 100 | Mtrs | 4095 | 12285
|  | Cost of Material for 100 Metres | [5 empty] | 12285
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 122.85
|  | Total Cost of Material + Labour Charges | [5 empty] | 154.4165
|  | Add Overhead @ 10.615% | [5 empty] | 16.3913
|  | Total Rate | [5 empty] | 170.8078
Elec 1.5.4 |  | Deduction of finalised item cost acc. to NOTE 2 : If FRLSH (FRLS) Wires are used instead of HFFR during execution of work, for arrig the FRLSH (FRLS) Flexible wires rates 15% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains.NOTE 3 : If Class - II conductor Wires are not used 5% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains. | [5 empty] | 136.6462
|  | Rounded off rate | [5 empty] | 137
Run of 3 of 4.0 Sq.mm Copper Cable
Data
24-25- RSD 3.1.5 |  | Rewiring with Supply and Run of 3 of 4.00 Sqmm HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. in existing pipe for run of mains inlcuding all labour charges etc., complete Copper cable Makes :Finolex / RR kabel / Havells / Polycab
Copper Cable Makes : Finolex / RR kabel / Havells / APAR EBXL / KEI (HFFR) / Polycab ((HR_FR-LF) / L&T / V-Guard (HFFR).
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 775 | 775
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 3 | day | 1 | day | 650 | 1950
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
|  | Labour for 100 Mtr | [5 empty] | 3375
|  | Labour for 1 Mtr | [5 empty] | 33.75
|  | Add GHMC Allowance @40% | [5 empty] | 13.5
|  | Labour subtotal | [5 empty] | 47.25
b) Material
ELEC-1.5.1-c | 4 | Supply of 4.00 Sqmm HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 300 | Mtrs | 100 | Mtrs | 6250 | 18750
|  | Cost of Material for 100 Metres | [5 empty] | 18750
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 187.5
|  | Total Cost of Material + Labour Charges | [5 empty] | 234.75
|  | Add Overhead @ 10.615% | [5 empty] | 24.9187
|  | Total Rate | [5 empty] | 259.6687
Elec 1.5.4 |  | Deduction of finalised item cost acc. to NOTE 2 : If FRLSH (FRLS) Wires are used instead of HFFR during execution of work, for arrig the FRLSH (FRLS) Flexible wires rates 15% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains. | [5 empty] | 220.7184
|  | Rounded off rate | [5 empty] | 221
Run of 5 of 6.0 Sq.mm Copper Cable
Data
24-25 RSD 3.1.6X2 |  | Rewiring with Supply and Run of 5 of (6.0 Sq.mm) HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. in existing pipe for run of mains inlcuding all labour charges etc., complete Copper cable Makes :Finolex / RR kabel / Havells / Polycab
Copper Cable Makes : Finolex / RR kabel / Havells / APAR EBXL / KEI (HFFR) / Polycab ((HR_FR-LF) / L&T / V-Guard (HFFR).
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 775 | 1550
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 6 | day | 1 | day | 650 | 3900
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
|  | Labour for 100 Mtr | [5 empty] | 6750
|  | Labour for 1 Mtr | [5 empty] | 67.5
|  | Add GHMC Allowance @40% | [5 empty] | 27
|  | Labour subtotal | [5 empty] | 94.5
b) Material
ELEC-1.5.1-d | 4 | Supply of6Sqmm HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 500 | Mtrs | 100 | Mtrs | 9230 | 46150
|  | Cost of Material for 100 Metres | [5 empty] | 46150
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 461.5
|  | Total Cost of Material + Labour Charges | [5 empty] | 556
|  | Add Overhead @ 10.615% | [5 empty] | 59.0194
|  | Total Rate | [5 empty] | 615.0194
Elec 1.5.4 |  | Deduction of finalised item cost acc. to NOTE 2 : If FRLSH (FRLS) Wires are used instead of HFFR during execution of work, for arrig the FRLSH (FRLS) Flexible wires rates 15% may be deducted from the finished Cost data of Light / Fan / Separate Plug Points and Run of mains. | [5 empty] | 522.7665
|  | Rounded off rate | [5 empty] | 523
Booster Pump
Data
Finished Item |  | Replacement and Supply, Installation, Testing and Commissioning of Pressure Boosting pump with 24 Ltr MS stand, Pressure Switch, Pressure Gauge and all standard fitings fully automatic ON / OFF system, 2900 RPM with stainless steel casing and impellar suitble for 1HPcapacity complete in all respects. Make : Grundfoss
a) Material
Elec.5..13.1.c | 1 | Supply, Installation, Testing and Commissioning of Pressure Boosting pump with 24 Ltr MS stand, Pressure Switch, Pressure Gauge and all standard fitings fully automatic ON / OFF system, 2900 RPM with stainless steel casing and impellar suitble for 1HPcapacity complete in all respects. Make : Grundfoss | 1 | Nos | 1 | Each | 38850 | 38850
|  | Cost of Material for Laying on wall for | [5 empty] | 38850
|  | Add Overhead @ 10.615% | [5 empty] | 4123.9275
|  | Total Rate | [5 empty] | 42973.9275
|  | Rounded off rate | [5 empty] | 42974
4Way TPN DB
Data
24-25 RSD 4.4.4A |  | Replacement of old u/s with new Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for and for 1 No 63A FP Isolator and 12 Nos 6-32 A 10kA SP MCBs as out goings of including internal connections and labour charges for Flush Mounting etc., complete DB Makes : Legrand / Schneider / Siemens MCB Makes : Legrand-DX3/ Schneider-Acti9 / Siemen
a) Labour charges for Flush Mounting
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 775 | 387.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 4 | Semi Skilled Mason. SOR-2025-26 Sl No 35 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
|  | Labour for 1 No | [5 empty] | 2337.5
|  | Add GHMC Allowance @40% | [5 empty] | 935
|  | Labour subtotal | [5 empty] | 3272.5
b) Material
ELEC-10.4.10 | 5 | Cement. | 12.5 | Kg | 1 | Kg | 9 | 112.5
ELEC-2.17.1-b | 6 | Supply of (8+12) 4 Way TPN DB Horizontal with IP 43, 12 Nos Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos S.P. out goings and for 1 No 4 pole Incommer etc complete ofMakes : Makes Legrand / Schneider / Siemens | 1 | Nos | 1 | No | 4830 | 4830
ELEC-2.15.1-g | 7 | Supply of 63A FP Isolator of Makes : Legrand-DX3/ Schneider-Acti9 / Siemen | 1 | Nos | 1 | No | 1512 | 1512
ELEC-2.14.1 -a | 2 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3/ Schneider-Acti9 / Siemen | 24 | No | 1 | No | 340 | 8160
|  | Cost of Material for 1 No | [5 empty] | 14614.5
|  | Total Cost of Material + Labour Charges | [5 empty] | 17887
|  | Add Overhead @ 10.615% | [5 empty] | 1898.705
|  | Total Rate | [5 empty] | 19785.7051
|  | Rounded off rate | [5 empty] | 19786
8way SPN DB
Data
24-25 RSD 4.4.2b |  | Replacement of old u/s with new Supply and fixing of 8 Way SPN DB with IP 43 Protection as per IS:13032 including Supply and Fixing of 1 No 40A DP Isolator and 6 Nos 6-32A 10kA ISI Marked C/D curve SP MCBs with all connections and labour charges etc., complete for flush Mounting/Surface . DBMakes :Legrand / Schneider / Siemens / LK / Havells Stadx / ABB / BCH Isolator Makes : Legrand-DX3/ Schneider-Acti9 / Siemen MCB Makes : Legrand-DX3/ Schneider-Acti9 / Siemen
LABOUR
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 775 | 387.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 650 | 325
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 4 | Semi Skilled Mason. SOR-2025-26 Sl No 35 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 650 | 325
|  | COST OF LABOUR for 1 no | [5 empty] | 1687.5
|  | Add GHMC Allowance @40% | [5 empty] | 675
|  | Labour Sub total | [5 empty] | 2362.5
MATERIAL
ELEC-10.4.10 | 5 | Cement. | 4 | Kg | 1 | Kg | 9 | 36
ELEC-2.16.1-d | 6 | Supply of8 Way SPN DB with IP 43, Nos - Protection as per IS:13032 and suitable for 8 S.P out goings and for 1 No Incomer with 100 A tinned copper busbar, neutral bar, earth bar and cable ties for cable management, fully shrouded neutral bar, din bars and detachable gland plate etccomplete with inter connections. Makes : Legrand / Schneider / Siemens / LK / Havells Stadx / ABB / BCH | 1 | Nos | 1 | No | 2310 | 2310
ELEC-2.15.1-b | 7 | Supply of 40A DP Isolator of DB Makes : Makes : Legrand-DX3/ Schneider-Acti9 / Siemen | 1 | Nos | 1 | No | 620 | 620
ELEC-2.14.1 -a | 2 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3/ Schneider-Acti9 / Siemen | 6 | No | 1 | No | 340 | 2040
|  | Cost of Material | [5 empty] | 4970
|  | Total Cost of Material + Labour Charges | [5 empty] | 7332.5
|  | Add Overhead @ 10.615% | [5 empty] | 778.3449
|  | Total Rate | [5 empty] | 8110.8449
|  | Rounded off rate | [5 empty] | 8111
25 Ltrs Water Heater (Geysers)
Data
Finished item |  | Replacement of old u/s with new Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type Vertical / Horizontal 230/250V single phase 2000watts ISI mark 5 Star rated water heater with ABS plastic body of 25 ltrs capacity to withstand up to 8.0 bar of water pressure including all standard accessories and dead weight pressure reducing valve on out let side, including cost of 2 Nos SS flexible braided hose pipe, testing and all labour charges etc., complete.Makes : Crompton / AO Smith/ Venus/ Havells or equivalent as approved by the Dept.
b) Material
ELEC-5.2.1 c | 1 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type Vertical / Horizontal 230/250V single phase 2000watts ISI mark 5 Star rated water heater with ABS plastic body of 25 ltrs capacity to withstand up to 8.0 bar of water pressure including all standard accessories and dead weight pressure reducing valve on out let side, including cost of 2 Nos SS flexible braided hose pipe, testing and all labour charges etc., complete of Makes : Crompton / AO Smith/ Venus/ Havells or equivalent as approved by the Dept. | 1 | No | 1 | No | 12735 | 12735
|  | Cost of Material | [5 empty] | 12735
|  | Add Overhead @ 10.615% | [5 empty] | 1351.8202
|  | Total Rate | [5 empty] | 14086.8203
|  | Rounded off rate | [5 empty] | 14087
Run of 1 of 1.50 Sq.mm
Data
24-25 RSD 3.1.2 |  | Rewiring with Supply and Run of 1 of 1 .5 Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable in existing pipe for UPS points inlcuding all labour charges etc., complete.Makes :Finolex / RR kabel / Havells / Polycab
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 775 | 263.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 650 | 221
|  | Labour for 100 Mtr | [5 empty] | 1134.5
|  | Labour for 1 Mtr | [5 empty] | 11.345
|  | Add GHMC Allowance @40% | [5 empty] | 4.538
|  | Labour subtotal | [5 empty] | 15.883
b) Material
ELEC-1.5.1-a | 4 | Supply of 1.5 Sqmm Class - II Conductor HFFR PVC insulated 1100V grade as per IS:694 /2010, IS 17048 specification for Copper cable. Makes :Finolex / RR kabel / Havells / Polycab | 100 | Mtrs | 100 | Mtr | 2530 | 2530
|  | Cost of Material for 100 Metres | [5 empty] | 2530
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 25.3
|  | Total Cost of Material + Labour Charges | [5 empty] | 41.183
|  | Add Overhead @ 10.615% | [5 empty] | 4.3716
45.5546
|  | Rounded of Rate | [5 empty] | 46
Independent earthing
Data
Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I ( Cast iron ) pipe with Flange 2.5m long enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with salt and charcoal from the bottom of the pipe giving earth connection from electrode through flange with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II)
ELEC -8.19.11 | 1 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I ( Cast iron ) pipe with Flange 2.5m long enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with salt and charcoal from the bottom of the pipe giving earth connection from electrode through flange with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II) | 1 | Nos | 1 | Nos | 9550 | 9550
|  | Cost of Finished item | [5 empty] | 9550
|  | Add Overhead @ 10.615% | [5 empty] | 1013.7325
|  | Total Cost of Material | [5 empty] | 10563.7325
|  | Rounded of Rate | [5 empty] | 10564
8 SWG GI Wire
Data
24-25 RSD 5.2.5/2 |  | Replacement of old u/s with new Supply and Run of No.8 SWG G.I wire including cost of all accessories and labour charges etc., complete. (0.104Kgs/1Mtr)
a) Labour charges :
| 1 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
|  | Labour for 100 Mtrs | [5 empty] | 1300
|  | Labour for 1 Mtr | [5 empty] | 13
|  | Labour Charges | [5 empty] | 13
|  | Add GHMC Allowance @40% | [5 empty] | 5.2
|  | Labour Sub total | [5 empty] | 18.2
b) Material
ELEC -10.3.6 | 2 | Supply aof No.8 SWG G.I wire. | 10.4 | Kgs | 1 | Kg | 119 | 1237.6
ELEC -10.1.4 | 3 | U Nails. | 1.5 | Nos | 100 | Nos | 44 | 0.66
|  | Cost of Material for 100 Metres | [5 empty] | 1238.26
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 12.3826
|  | Total Cost of Material + Labour Charges | [5 empty] | 30.5826
|  | Add Overhead @ 10.615% | [5 empty] | 3.2463
|  | Tota1 | [5 empty] | 33.8289
|  | Rounded of Rate | [5 empty] | 34
Starter for Motors
Data
Finished item |  | Replacement of u/s with new Supply & Fixing of D.O.L Starter 250V, Single phase, 50Hz. With Sheet Steel enclouser comprising of contactor with bi-metalic relay with neceSheet Steelary push buttons, etc., complete suitable upto 3 H.P Makes: Siemens / LK / BCH
b) Material
ELEC-5.5.1-a | 1 | Replacement of u/s with new Supply & Fixing of D.O.L Starter 250V, Single phase, 50Hz. With Sheet Steel enclouser comprising of contactor with bi-metalic relay with neceSheet Steelary push buttons, etc., complete suitable upto 3 H,P Makes: Siemens / LK / BCH | 1 | Nos | 1 | Nos | 2400 | 2400
|  | Cost of Material | [5 empty] | 2400
|  | Add Overhead @ 10.615% | [5 empty] | 254.76
|  | Total | [5 empty] | 2654.76
|  | Rounded of Rate | [5 empty] | 2655
1.50 HP Borewell Pumpset
Data
Finished item |  | Replacement of u/s with new Supply and Transportation of 1.5 HP 21 stage single phase ISI submersible motor pumpset suitable for 4" Bore well. Makes: Texmo / CRI / Falcon
b) Material
ELEC-5.8.1.b | 1 | Supply,Transportation and fixing of 1.50HP Single phase open well ISI submersible motor pumpset of make Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon | 1 | Nos | 1 | Nos | 20265 | 20265
|  | Cost of Material | [5 empty] | 20265
|  | Add Overhead @ 10.615% | [5 empty] | 2151.1298
|  | Total | [5 empty] | 22416.1298
|  | Rounded of Rate | [5 empty] | 22416
1.50 HP Monoblock
Data
Finished item |  | Repalcement of u/s with new Supply and Transportation of 1.5 HP (32x25mm) Single phase ISI Mono block CI body motor pumpset including starter and all labour charges. Makes: Texmo / CRI / Falcon
b) Material
ELEC-5.6.1-d | 1 | Supply and Transportation of 1.5 HP (32x25mm) Single phase ISI Mono block CI body motor pumpset. Makes: Texmo / CRI / Falcon | 1 | Nos | 1 | Nos | 21000 | 21000
|  | Cost of Material | [5 empty] | 21000
|  | Add Overhead @ 10.615% | [5 empty] | 2229.15
|  | Total | [5 empty] | 23229.15
|  | Rounded of Rate | [5 empty] | 23229
GI Strip
Data
24-25-27.1.7 |  | Replacement of old u/s with new Supply and Run of 50mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. (2.36Kgs/1Mtr) (SD 5.2.7)
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 775 | 1550
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
|  | Labour for 100 Mtrs | [5 empty] | 2850
|  | Labour for 1 Mtr | [5 empty] | 28.5
b) Material
ELEC -10.3.6 | 3 | G.I. Strip / Plate / Wire (per K. G). | 236 | Kgs | 1 | Kg | 119 | 28084
| 4 | Sundries.
|  | Cost of Material for 100 Metres | [5 empty] | 28084
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 280.84
|  | Total Cost of Material + Labour Charges | [5 empty] | 309.34
|  | Add Overhead @ 10.615% | [5 empty] | 32.8364
|  | Total | [5 empty] | 342.1764
|  | Rounded of Rate | [5 empty] | 342
Flood Light
Data
SD-NA |  | Replacement an Supply and transportation and Fixing of 150 W +/-10% (>=15000 Lumens) LED Flood light Luminaire made of pressure die cast aluminum housing with powder coated, having toughened glass cover, Suitable lens on LEDs, IP 66 (Silicon gasket ensures Optical & Electrical compartments are IP 66 ) protected, wide operating voltage range , P.F > 0.90, System having efficacy >110 lumens/watt, with Ingress protection IP66, Driver surge protection >10KV, THD<15%, CCT: 3000- 6500K as desired by the department and as per IS, CRI>70, Inbuilt Electricalprotections like Over voltage, short circuit, Over load, Open Circuit, Miswiring, etc complete with BIS certification with 2 years warranty.LUMINAIRE MAKE : Philips / Crompton / Bajaj / Wipro LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs.
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.1 | day | 1 | day | 775 | 77.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 650 | 65
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.1 | day | 1 | No | 650 | 65
|  | Labour for 1 No | [5 empty] | 207.5
|  | Add GHMC Allowance @40% | [5 empty] | 83
|  | Labour Sub total | [5 empty] | 290.5
b) Material
ELEC-3.5.4-d | 8 | Supply and transportation of 150 W +/-10% (>=15000 Lumens) LED Flood light Luminaire made of pressure die cast aluminum housing with powder coated, having toughened glass cover, Suitable lens on LEDs, IP 66 (Silicon gasket ensures Optical & Electrical compartments are IP 66 ) protected, wide operating voltage range , P.F > 0.90, System having efficacy >110 lumens/watt, with Ingress protection IP66, Driver surge protection >10KV, THD<15%, CCT: 3000- 6500K as desired by the department and as per IS, CRI>70, Inbuilt Electricalprotections like Over voltage, short circuit, Over load, Open Circuit, Miswiring, etc complete with BIS certification with 5 years warranty. The contractor has to furnish the manufacturer warranty letter, LM 79 and LM 80 certificates.LUMINAIRE MAKE Philips / Crompton / Bajaj / Wiprot LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs. | 1 | Nos | 1 | Nos | 11218 | 11218
|  | Deduct 30% cost for 2 Years Warrenty | [5 empty] | 3365.4
|  | Cost of Material for 1 No | [5 empty] | 7852.6
|  | Total Cost of Material + Labour Charges | [5 empty] | 8143.1
|  | Add Overhead @ 10.615% | [5 empty] | 864.3901
|  | Total Rate | [5 empty] | 9007.4901
|  | Rounded off rate | [5 empty] | 9007
Thermo Plastic Box with Switch gear
Data
Replacement of old u/s with new Supply and fixing of 200X150X100 thermo plastic pole boxes IP 65 protection.Make : Hensel / Sintex / Sadhrish / EPP or including Supply and Fixing of 1 Nos 6-32A SP mcb 10kA ISI Marked C/D curve SP MCBs with all connections and labour charges etc., complete for SurfaceMounting of MCB Makes : Legrand-DX3 / Schneider-Acti9.
LABOUR
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skiiled Labour rates. | 0.1 | day | 1 | day | 775 | 77.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 650 | 65
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 650 | 65
|  | COST OF LABOUR for 1 no | [5 empty] | 207.5
|  | Add GHMC Allowance @40% | [5 empty] | 83
|  | Labour Sub total | [5 empty] | 290.5
MATERIAL
| 4 | Supply of 200X150X100 thermo plastic pole boxes IP 65 protection.
ELEC-8.13.1a |  | Make : Hensel / Sintex / Sadhrish / EPP or equivalent | 1 | Nos | 1 | No | 875 | 875
ELEC-2.14.1 -a | 2 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3/ Schneider-Acti9 / Siemen | 1 | No | 1 | No | 340 | 340
|  | Cost of Material | [5 empty] | 1215
|  | Total Cost of Material + Labour Charges | [5 empty] | 1505.5
|  | Add contractor overheads@10.615% | [5 empty] | 159.8088
|  | Total | [5 empty] | 1665.3088
|  | Rounded off rate | [5 empty] | 1665
4 Core x 4 Sqmm Armoured Cable
Data
Finished item |  | Rewiring with Supply and Laying of 4 core 4 Sqmm PVC / XLPE Insulated, Armoured Copper cable as per IS 7098 / Part-I / 1988 including all transportation charges etc complete of Makes : Finolex / RR kabel / Havells / Polycab
b) Material
ELEC-1.5.7-o | 1 | Supply of 4 core 4 Sqmm PVC / XLPE Insulated, Armoured Copper cable as per IS 7098 / Part-I / 1988 including all transportation charges etc complete of Makes : Finolex / RR kabel / Havells / Polycab | 1 | Mtrs | 1 | Mtrs | 319 | 319
|  | Cost of Material | [5 empty] | 319
Provisional rate | 2 | Labour for laying | 1 | Mtrs | 1 | Mtrs | 6 | 6
|  | Total Cost of Material + Labour Charges | [5 empty] | 325
|  | Add contractor overheads@10.615% | [5 empty] | 34.4988
|  | Total Rate | [5 empty] | 359.4987
|  | Rounded off rate | [5 empty] | 359
50 Sqmm 3.5 core Cable
Data
Finished item |  | Replacement of old u/s with new Supply of 50 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes : Torrent / Polycab / Havells / RR kable
b) Material
ELEC-4.1.1 i |  | Supply of 50 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes : Torrent / Unicab / Universal / Polycab / Havells / KEI / RR kable | 1 | Mtrs | 1 | Mtr | 600 | 600
|  | Add contractor overheads@10.615% | [5 empty] | 63.69
|  | Total Rate | [5 empty] | 663.69
|  | Rounded off rate | [5 empty] | 664
Laying of 50 Sqmm Cable
Data
24-25 RSD 15.6.3 |  | Laying of PVC armoured under ground cable 3.5 Core 50 Sqmm fixing on chromium plated metallic base saddles on wall as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete.
b) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 775 | 775
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 4 | day | 1 | day | 650 | 2600
|  | Labour Charges for 100 Mtrs | [5 empty] | 3375
|  | Labour Charges for 1 Mtr | [5 empty] | 33.75
|  | Add GHMC Allowance @40% | [5 empty] | 13.5
|  | Labour Sub total | [5 empty] | 47.25
a) Material
Elec-1.4.4 e | 3 | Supply of No.8 Screws of 50mm.(SOR-2025-26-Elec-1.4.4 e) | 400 | Nos | 100 | Nos | 163 | 652
Elec-10.4.23.f | 4 | Supply of Saddle / Clamps suitable for fixing 3.5 Core 50 Sqmm Cable (SOR-2025-26 ELEC-10.4.23 f) | 200 | Nos | 100 | Nos | 668 | 1336
|  | Cost of Material for laying of cable for 100mtr | 100 | Mtrs |  |  |  | 1988
|  | Cost of Material for laying of cable for 1 mtr | 1 | Mtrs |  |  |  | 19.88
|  | Total Cost of Material + Labour Charges | [5 empty] | 67.13
|  | Add contractor overheads@10.615% | [5 empty] | 7.1258
|  | Total Rate | [5 empty] | 74.2558
|  | Rounded off rate | [5 empty] | 74
Earthwork excavation of UG Cable
Data
24-25 RSD 15.6.1 |  | Earth work excavation of Trench in hard ground soil upto a depth of 0.9 mts and laying of U.G cables up to 50 sqmm covering the cable with bricks and back filling of Trench including cost and conveyance of materials and labour charges etc., complete..
b) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 775 | 775
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
| 3 | Man Mazdoor -UN-SKILLED CATEGORYSOR-2025-26 III :item Nos 3/4 | 2.5 | day | 1 | day | 650 | 1625
|  | Labour Charges for 100 Mtrs | [5 empty] | 3700
|  | Labour Charges for 1 Mtr | [5 empty] | 37
|  | Add GHMC Allowance @40% | [5 empty] | 14.8
|  | Labour Sub total | [5 empty] | 51.8
a) Material
ELEC-10.4.15 | 4 | Earth Work Excavation (ELEC-10.4.15) | 27 | Cum | 1 | Cum | 318 | 8586
100 x 0.3 x 0.90 Cu. Mtrs
ELEC-10.4.12 | 5 | Bricks ELEC-10.4.12 | 920 | Nos | 1000 | Nos | 9702 | 8925.84
|  | Cost of Material for laying of cable in trench for 1mtr | 100 | Mtrs |  |  |  | 17511.84
|  | Cost of Material for laying of cable in trench for 1 mtr | 1 | Mtrs |  |  |  | 175.1184
|  | Total Cost of Material + Labour Charges | [5 empty] | 226.9184
|  | Add contractor overheads@10.615% | [5 empty] | 24.0874
|  | Total Rate | [5 empty] | 251.0058
|  | Rounded off rate | [5 empty] | 251
35 Sqmm Cable
Data
Finished item |  | Replacement of old u/s with new Supply of 35 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Makes : Makes :Torrent / Polycab / Havells / RR kable
b) Material
ELEC-4.1.1h | 1 | Supply of 35 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes :Makes :Torrent / Polycab / Havells / RR kabl | 1 | Mtrs | 1 | Mtr | 452 | 452
|  | Cost of Material | [5 empty] | 452
|  | Add contractor overheads@10.615% | [5 empty] | 47.9798
|  | Total Rate | [5 empty] | 499.9798
|  | Rounded off rate | [5 empty] | 500
25 Sqmm Cable
Data
Finished item |  | Replacement of old u/s with new Supply of 25 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Makes :Makes :Torrent / Polycab / Havells / RR kable
b) Material
ELEC-4.1.1g | 1 | Supply of 25 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Makes : Makes :Torrent / Polycab / Havells / RR kabl | 1 | Mtrs | 1 | Mtr | 378 | 378
|  | Cost of Material | [5 empty] | 378
|  | Add contractor overheads@10.615% | [5 empty] | 40.1247
|  | Total Rate | [5 empty] | 418.1247
|  | Rounded off rate | [5 empty] | 418
Laying of 35 & 25 Sqmm Cable
Data
24-25 RSD 15.6.3 |  | Laying of PVC armoured under ground cable 3.5 Core 25&35 Sqmm fixing on chromium plated metallic base saddles on wall as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete.
b) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 775 | 775
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 4 | day | 1 | day | 650 | 2600
|  | Labour Charges for 100 Mtrs | [5 empty] | 3375
|  | Labour Charges for 1 Mtr | [5 empty] | 33.75
|  | Add GHMC Allowance @40% | [5 empty] | 13.5
|  | Labour Sub total | [5 empty] | 47.25
a) Material
Elec-1.4.4 d | 3 | Supply of No.8 Screws of 35mm. | 400 | Nos | 100 | Nos | 142 | 568
Elec-10.4.23 d | 4 | Supply of Saddle / Clamps suitable for fixing 3.5 Core 25&35 Sqmm Cable. | 200 | Nos | 100 | Nos | 468 | 936
|  | Cost of Material for laying of cable for 100mtr | 100 | Mtrs |  |  |  | 1504
|  | Cost of Material for laying of cable for 1 mtr | 1 | Mtrs |  |  |  | 15.04
|  | Total Cost of Material + Labour Charges | [5 empty] | 62.29
|  | Add contractor overheads@10.615% | [5 empty] | 6.6121
|  | Total Rate | [5 empty] | 68.9021
|  | Rounded off rate | [5 empty] | 69
8 Way VTPN DB
Data
24-25 RSD 4.4.4A |  | Replacement of old u/s with new Supply of 8 Way VTPN DB with IP 43 Protection as per IS:13032 and suitable for accommodating 8 Nos 63 A T.P. MCBs as out goings and 125A 4 pole MCCB as Incomer with 250 A tinned copper busbar, neutral bar, earth bar and cable ties for cable management, fully shrouded neutral bar, profile blanking modules for unused MCB ways, din bars and detachable gland plate etc complete with inter connections. Makes : Legrand / Schneider / Siemens
a) Labour charges for Flush Mounting
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 775 | 387.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 4 | Semi Skilled Mason. SOR-2025-26 Sl No 35 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
|  | Labour for 1 No | [5 empty] | 2337.5
|  | Add GHMC Allowance @40% | [5 empty] | 935
|  | Labour subtotal | [5 empty] | 3272.5
b) Material
ELEC-10.4.10 | 5 | Cement. | 12.5 | Kg | 1 | Kg | 9 | 112.5
ELEC-2.17.3-c | 6 | Supply of 8 Way VTPN DB with IP 43 Protection as per IS:13032 and suitable for accommodating 8 Nos 63 A T.P. MCBs as out goings and 125A / 160A 4 pole MCCB as Incomer with 250 A tinned copper busbar, neutral bar, earth bar and cable ties for cable management, fully shrouded neutral bar, profile blanking modules for unused MCB ways, din bars and detachable gland plate etc complete with inter connections. Makes : Legrand / Schneider / Siemens | 1 | Nos | 1 | No | 20895 | 20895
ELEC-2.8.1-d | 7 | Supply of 125A 4 Pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : Schneider-NS NSX/Legrand -DP X3/ Siemens-3V | 1 | Nos | 1 | No | 13770 | 13770
ELEC-2.14.1 -i | 2 | Supply of 50-63 A TP MCB 10 kA, C/D Curve ISI Mark. Makes : Legrand-DX3 / Schneider-Acti9/ Siemens | 8 | Nos | 1 | No | 2494 | 19952
|  | Cost of Material for 1 No | [5 empty] | 54729.5
|  | Total Cost of Material + Labour Charges | [5 empty] | 58002
|  | Add Overhead @ 10.615% | [5 empty] | 6156.9123
|  | Total Rate | [5 empty] | 64158.9123
|  | Rounded off rate | [5 empty] | 64159
3 Core x 2.5 Sqmm Armoured Cable
Data
Finished item |  | Rewiring with Supply and Laying of 6.0 Sqmm 4 Core PVC / XLPE Insulated, Armoured Copper cable as per IS 7098 / Part-I / 1988 including all transportation charges etc complete of Makes : Finolex / RR kabel / Havells / Polycab
b) Material
ELEC-1.5.7-p | 1 | Supply of 6.0 Sqmm 4 Core PVC / XLPE Insulated, Armoured Copper cable as per IS 7098 / Part-I / 1988 including all transportation charges etc complete of Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI / Gloster / V-Guard / Finecab / SPM/ Gemini / Unistar / Windsor / Payal / Fortune Arrt / Avocab / Nakoda / HPL / Sudhakar / Bonton / Rajnigandha / Pawancab / South King. | 1 | Mtrs | 1 | Mtrs | 440 | 440
|  | Cost of Material | [5 empty] | 440
Provisional rate | 2 | Labour for laying | 1 | Mtrs | 1 | Mtrs | 6 | 6
|  | Total Cost of Material + Labour Charges | [5 empty] | 446
|  | Add Overhead @ 10.615% | [5 empty] | 47.3429
|  | Total Rate | [5 empty] | 493.3429
|  | Rounded off rate | [5 empty] | 493
8way SPN DB
Data
24-25 RSD 4.4.2b |  | Replacement of old u/s with new Supply and fixing of 8 Way SPN DB with IP 43 Protection as per IS:13032 including Supply and Fixing of 1 No 50-63A 10KA FP MCB and 4 Nos 6-32A 10kA ISI Marked C/D curve SP MCBs with all connections and labour charges etc., complete for flush Mounting/Surface . DBMakes :Legrand / Schneider / Siemens / LK / Havells Stadx / ABB / BCH MCB Makes : Legrand-DX3/ Schneider-Acti9 / Siemen
LABOUR
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 775 | 387.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 650 | 325
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 4 | Semi Skilled Mason. SOR-2025-26 Sl No 35 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 650 | 325
|  | COST OF LABOUR for 1 no | [5 empty] | 1687.5
|  | Add GHMC Allowance @40% | [5 empty] | 675
|  | Labour Sub total | [5 empty] | 2362.5
MATERIAL
ELEC-10.4.10 | 5 | Cement. | 4 | Kg | 1 | Kg | 9 | 36
ELEC-2.16.1-d | 6 | Supply of8 Way SPN DB with IP 43, Nos - Protection as per IS:13032 and suitable for 8 S.P out goings and for 1 No Incomer with 100 A tinned copper busbar, neutral bar, earth bar and cable ties for cable management, fully shrouded neutral bar, din bars and detachable gland plate etccomplete with inter connections. Makes : Legrand / Schneider / Siemens / LK / Havells Stadx / ABB / BCH | 1 | Nos | 1 | No | 2310 | 2310
ELEC-2.14.1 -L | 3 | Supply of 50-63A 10KA FP MCB, C/D Curve ISI Mark of make Legrand-DX3/ Schneider-Acti9 / Siemen | 1 | No | 1 | No | 3310 | 3310
ELEC-2.14.1 -a | 2 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3/ Schneider-Acti9 / Siemen | 4 | No | 1 | No | 340 | 1360
|  | Cost of Material | [5 empty] | 6980
|  | Total Cost of Material + Labour Charges | [5 empty] | 9342.5
|  | Add Overhead @ 10.615% | [5 empty] | 991.7064
|  | Total Rate | [5 empty] | 10334.2064
|  | Rounded off rate | [5 empty] | 10334
Labour charges for dressing and rectification of cables
Data
Labour charges for dressing of electrical cables ,internet cables and rectification of the existing fixtures and circuits
LABOUR
SOR 2025-26 | 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 5 | day | 1 | day | 775 | 3875
| 4 | Semi Skilled Mason. SOR-2025-26 Sl No 35 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
|  | COST OF LABOUR for 1 no | [5 empty] | 4525
|  | Labour Sub total | [5 empty] | 4525
|  | Labour Charges | [5 empty] | 4525
|  | Add Overhead @ 10.615% | [5 empty] | 480.3287
|  | Total Rate | [5 empty] | 5005.3287
|  | Rounded off rate | [5 empty] | 5005
Cat 6 Cable
Data
Finished item |  | Supply of LAN Cable cat - 6 UTP cable. Makes : D Link / AMP / Molex / Legrand / Krone.
b) Material
ELEC-9.1.3A | 1 | Supply of LAN Cable cat - 6 UTP cable. Makes : D Link / AMP / Molex / Legrand / Krone. | 100 | Mtrs | 100 | Mtrs | 3066 | 3066
|  | Cost of Material for 100 Metres | [5 empty] | 3066
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 30.66
|  | Add Overhead @ 10.615% | [5 empty] | 3.2546
|  | Total rate | [5 empty] | 33.9146
|  | Rounded off rate | [5 empty] | 34
Data 47
8 Port D-Link
Data
Finished item |  | Supply and fixing of 8 Port 10 / 100 / 1000 Gigabit Unmanageable Ethernet switch. Makes : TP Link / D link / Netfox.
b) Material
ELEC-9.1.7.C | 1 | Supply and fixing of 8 Port D-Link DGS-1008A 8-Port Gigabit Easy Desktop Switch (White) of Makes : D link including all connections. (Approved rate from MRC Qtrs) | 1 | Nos | 1 | Nos | 2289 | 2289
|  | Cost of Material | [5 empty] | 2289
|  | Add Overhead @ 10.615% | [5 empty] | 242.9774
|  | Total rate | [5 empty] | 2531.9774
|  | Rounded off rate | [5 empty] | 2532
3 feet length moulded patch cord.
Data
Finished item |  | Supply of 3 feet length moulded patch cord. Makes : D Link / Legrand /TP link/Digisol.
b) Material
ELEC-9.1.10b | 1 | Supply of 3 feet length moulded patch cord. Makes : D Link / Legrand /TP link/Digisol. | 1 | Nos | 1 | Nos | 184 | 184
|  | Cost of Material | [5 empty] | 184
|  | Add Overhead @ 10.615% | [5 empty] | 19.5316
|  | Total rate | [5 empty] | 203.5316
|  | Rounded off rate | [5 empty] | 204
6 U Wall Rack
Data
Finished item |  | Supply and installation of 6U wall 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK 08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilever shelf etc., complete. Makes : Vallrack (Legrand) / Netrack.
b) Material
ELEC-9.1.16 | 1 | Supply and installation of 6U wall 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK 08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilever shelf etc., complete. Makes : Vallrack (Legrand) / Netrack. | 1 | No | 1 | No | 7392 | 7392
|  | Cost of Material for 1 No | [5 empty] | 7392
|  | Add Overhead @ 10.615% | [5 empty] | 784.6608
|  | Total rate | [5 empty] | 8176.6608
|  | Rounded off rate | [5 empty] | 8177
Rg-6 Cable
Data
NA SD |  | Supply and Run of 1 of RG-6 Cu flexible ISI mark coaxial foarmed cable in existing pipe for TV's inlcuding all labour charges etc., complete of make Finolex/ RR Kable
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 775 | 263.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 650 | 221
|  | Labour for 100 Mtr | [5 empty] | 1134.5
|  | Labour for 1 Mtr | [5 empty] | 11.345
|  | Add GHMC Allowance @40% | [5 empty] | 4.538
|  | Labour subtotal | [5 empty] | 15.883
b) Material
Pricelist | 4 | Supply of of 1 of RG-6 Cu flexible ISI mark coaxial foarmed cable make Finolex/ RR Kable (Approved rate from MRC Qtrs) | 100 | Mtrs | 1 | Mtrs | 22 | 2200
|  | Cost of Material for 100 Metres | [5 empty] | 2200
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 22
|  | Total Cost of Material + Labour Charges | [5 empty] | 37.883
|  | Add Overhead @ 10.615% | [5 empty] | 4.0213
|  | Total rate | [5 empty] | 41.9043
|  | Rounded off rate | [5 empty] | 42
Information Outlets
Data
24-25 RSD 2.1.4 |  | Supply and fixing of Cat 6 RJ-45 information outlets including -single face plate on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : D Link / AMP / Molex / Legrand / Krone.
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 775 | 25.575
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 650 | 21.45
|  | Labour for 1 Point | [5 empty] | 47.025
|  | Add GHMC allowance @40% | [5 empty] | 18.81
|  | Labour Sub total | [5 empty] | 65.835
b) Material
Elec-1.3.1-a | 3 | Supply of 1 or 2 Module box. | 1 | Nos | 1 | No | 84 | 84
ELEC-1.3.4.a | 4 | Supply of 1 or 2 Modular Cover Frame
|  | Makes Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 75 | 75
ELEC-9.1.5.b | 5 | Supply of Cat 6 RJ-45 information outlets including -Single face plate of Makes : D Link / AMP / Molex / Legrand / Krone. | 1 | Nos | 1 | No | 305 | 305
|  | Total material cost | [5 empty] | 464
|  | Total Material and Labour charges for 1 no | [5 empty] | 529.835
|  | Add Overhead @ 10.615% | [5 empty] | 56.242
|  | Total rate | [5 empty] | 586.077
|  | Rounded off rate | [5 empty] | 586
Modular co-Axial socket type TV
Data
24-25 RSD 2.1.4 |  | Supply and fixing of Modular co-Axial socket type TV Antenna outlet on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 775 | 25.575
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 650 | 21.45
|  | Labour for 1 Point | [5 empty] | 47.025
|  | Add GHMC allowance @40% | [5 empty] | 18.81
|  | Labour Sub total | [5 empty] | 65.835
b) Material
ELEC-1.3.1.a | 3 | Supply of 1 or 2 Module box. SOR-2025-26 | 1 | Nos | 1 | No | 84 | 84
| 4 | Supply of 1 or 2 Modular Cover Frame.SOR-2025-26()
ELEC-1.3.4.a |  | Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 75 | 75
ELEC-1.9.2 p | 5 | Supply of Modular co-Axial socket type TV Antenna outlet. Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 89 | 89
|  | Total material cost | [5 empty] | 248
|  | Total Material and Labour charges for 1 no | [5 empty] | 313.835
|  | Add Overhead @ 10.615% | [5 empty] | 33.3136
|  | Total rate | [5 empty] | 347.1486
|  | Rounded off rate | [5 empty] | 347
Patch panel
Data
Finished item |  | Supply and fixing of unloaded 24 port patch panel with IO separate Makes : Digisol / TP Link / D link. / Legrand
b) Material
ELEC-9.1.11 | 1 | Supply and fixing of unloaded 24 port patch panel with IO separate Makes : Digisol / TP Link / D link. / Legrand | 1 | No | 1 | No | 7004 | 7004
|  | Cost of Material for 1 No | [5 empty] | 7004
|  | Add Overhead @ 10.615% | [5 empty] | 743.4746
|  | Total rate | [5 empty] | 7747.4746
|  | Rounded off rate | [5 empty] | 7747
1.8/2.0 TR Split AC's
Data
NA-SD |  | Replacement of old u/s with new Supply,Transportation,Installation testing and commissioning of INVERTER Model Cool type split AC unit 2.0/1.8 TR 5 Star capable of delivering 21600 BTU/hr and above with operating on refrigerant R-32 / R-410 Makes : Daikin / Toshibha / Carrier / Blue Star / Hitachi / LG / Samsung / Lloyd or equivalent with high wall mounted Single Split indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing Heat cool dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 4 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with warranty of compressor for 5 years including MS bracket / MS angle iron stand with pads suitable for fixing out door unit of split AC unit with Warranty and CMC for Two years.
b) Material
ELEC-6.1.1-d | 1 | Supply,Transportation,Installation testing and commissioning of INVERTER Model Cool type split AC unit 2.0/1.8 TR 5 Star capable of delivering 21600 BTU/hr and above with operating on refrigerant R-32 / R-410 Makes : Daikin / Toshibha / Carrier / Blue Star / Hitachi / LG / Samsung / Lloyd or equivalent with high wall mounted Single Split indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing Heat cool dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 4 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with warranty of compressor for 5 years including MS bracket / MS angle iron stand with pads suitable for fixing out door unit of split AC unit with Warranty and CMC for Two years. | 1 | Nos | 1 | Nos | 54000 | 54000
ELEC-6.7.28 | 2 | Installation of Split Air Conditioners. | 1 | Nos | 1 | Nos | 1760 | 1760
ELEC-6.7.1 | 3 | Supply, Fabrication of 1set MS bracket suitable for fixing out door unit of split AC Unit. | 1 | Nos | 1 | Nos | 960 | 960
|  | Cost & installation of Unit | [5 empty] | 56720
|  | Add Overhead @ 10.615% | [5 empty] | 6020.828
|  | Total rate | [5 empty] | 62740.828
|  | Rounded off rate | [5 empty] | 62741
1.5 TR Split AC's
Data
NA-SD |  | Replacement of old u/s with new Supply,Transportation,Installation testing and commissioning of INVERTER Model Cool type split AC unit 1.5 TR 5 Star capable of delivering 18000 BTU/hr and above with operating on refrigerant R-32 / R-410 Makes : Daikin / Toshibha / Carrier / Blue Star / Hitachi / LG / Samsung / Lloyd or equivalent with high wall mounted Single Split indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing Heat cool dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 4 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with warranty of compressor for 5 years including MS bracket / MS angle iron stand with pads suitable for fixing out door unit of split AC unit with Warranty and CMC for Two years.
b) Material
ELEC-6.1.1-b | 1 | Supply,Transportation,Installation testing and commissioning of INVERTER Model Cool type split AC unit 1.5 TR 5 Star capable of delivering 18000 BTU/hr and above with operating on refrigerant R-32 / R-410 Makes : Daikin / Toshibha / Carrier / Blue Star / Hitachi / LG / Samsung /Lloyd or equivalent with high wall mounted Single Split indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing Heat cool dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 4 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with warranty of compressor for 5 years including MS bracket / MS angle iron stand with pads suitable for fixing out door unit of split AC unit with Warranty and CMC for Two years. | 1 | Nos | 1 | Nos | 44000 | 44000
ELEC-6.7.28 | 2 | Installation of Split Air Conditioners. | 1 | Nos | 1 | Nos | 1760 | 1760
ELEC-6.7.1 | 3 | Supply, Fabrication of 1set MS bracket suitable for fixing out door unit of split AC Unit. | 1 | Nos | 1 | Nos | 960 | 960
|  | Cost & installation of Unit | [5 empty] | 46720
|  | Add Overhead @ 10.615% | [5 empty] | 4959.328
|  | Total rate | [5 empty] | 51679.328
|  | Rounded off rate | [5 empty] | 51679
Copper Pipe
Data
Finished item |  | Replacement of old u/s with new Providing Additional 2 runs of 3/4" x 3/8" or 5/8" x 1/4" or 1/2"x 1/4" Copper tubes for suction and liquid between indoor and outdoor unit suitable size for Split Air-Conditioner including foaming, wrapping etc.,complete
b) Material
ELEC-6.7.2-a | 1 | Providing Additional 2 runs of 3/4" x 3/8" or 5/8" x 1/4" or 1/2"x 1/4" Copper tubes for suction and liquid between indoor and outdoor unit suitable size for Split Air-Conditioner including foaming, wrapping etc.,complete. | 1 | Nos | 1 | Nos | 990 | 990
|  | Add Overhead @ 10.615% | [5 empty] | 105.0885
|  | Cost of Material | [5 empty] | 1095.0885
Total rate
|  | Rounded off rate | [5 empty] | 1095
4.0 Sqmm 4 Core
Data
25 Sqmm Laying Half Labour Charges |  | Rewiring with Supply and Laying of 4.0 Sqmm 4 CoreP PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:2010 includingalltransportation charges etc complete. Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI / Gloster / V-Guard / Finecab / SPM / Gemini / Unistar / Windsor / Payal / Fortune Arrt / Avocab / Pawancab / Nakoda / HPL / Sudhakar / Bonton / Rajnigandha
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 775 | 387.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
|  | Labour Charges for 100 Mtrs | [5 empty] | 1687.5
|  | Labour Charges for 1 Mtr | [5 empty] | 16.875
|  | Add GHMC Allowance @40% | [5 empty] | 6.75
|  | Labour Sub total | [5 empty] | 23.625
b) Material
ELEC-1.5.5-u | 3 | Supply of 4.0 Sqmm 4 CoreP PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:2010 includingalltransportation charges etc complete. Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI / Gloster / V-Guard / Finecab / SPM / Gemini / Unistar / Windsor / Payal / Fortune Arrt / Avocab / Pawancab / Nakoda / HPL / Sudhakar / Bonton / Rajnigandha | 1 | Mtr | 1 | Mtr | 292 | 292
|  | Cost of Material | [5 empty] | 292
|  | Total Material and Labour charges for 1 mts | [5 empty] | 315.625
|  | Add Overhead @ 10.615% | [5 empty] | 33.5036
|  | Cost of Material | [5 empty] | 349.1286
|  | Rounded off rate | [5 empty] | 349
CPVC Pipe
Data
Finished item |  | Replacement of old u/s with new Supply, installation, testing and commissioning of the drain line with CPVC pipes of premium make of 28.60mm OD Pipe- SDR 13.5.
b) Material
TBSP-J.III-03 | 1 | Supply of premium make CPVC Pipes of 28.60mm OD Pipe- SDR 13.5. | 1 | Nos | 1 | Nos | 166 | 166
|  | Cost of Material | [5 empty] | 166
|  | Add Overhead @ 10.615% | [5 empty] | 17.6209
|  | Cost of Material | [5 empty] | 183.6209
|  | Rounded off rate | [5 empty] | 184
Core Cuttting
Data
Making core cutting to existing wall and chipping to the existing wall for providing drain piping and copper piping for providing new air conditioners units including all labour charges etc complete.
b) Material
Approved rate | 1 | Making core cutting to existing wall and chipping to the existing wall for providing drain piping and copper piping for providing new air conditioners units including all labour charges etc complete. (Approved Rate MRC Qtr No 4) | 1 | Nos | 1 | Nos | 550 | 550
|  | Cost of Material | [5 empty] | 550
|  | Rounded off rate | [5 empty] | 550
EPABX System
Data
Finished Item |  | IP Based digtal Telephone (EPABX) system complied with following specifications: > IP @ Core, PCM/TDM, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console, > Must support Mobile SIP (Android and I.O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt Call Details Software with search engine software > 4 Analog Trunks > 6 Digital Extensions > 32 Analog Extensions > 1 Digital Key Phone with minimum 16 Keys (Must work only on 2 wires) > Expandable to 64 Analog Extensions or more Makes: NEC / Alcatel
b) Material
Elec-9.3.1 | 1 | IP Based digtal Telephone (EPABX) system complied with following specifications: > IP @ Core, PCM/TDM, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console, > Must support Mobile SIP (Android and I.O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt Call Details Software with search engine software > 4 Analog Trunks > 6 Digital Extensions > 32 Analog Extensions > 1 Digital Key Phone with minimum 16 Keys (Must work only on 2 wires) > Expandable to 64 Analog Extensions or more Makes: NEC / Alcatel | 1 | No | 1 | No | 130000 | 130000
|  | Cost of Material for 1 No | [5 empty] | 130000
|  | Add Overhead @ 10.615% | [5 empty] | 13799.5
|  | Cost of Material | [5 empty] | 143799.5
|  | Rounded off rate | [5 empty] | 143800
Digital Key Telephone with 2 line display
Data
Digital Key Telephone with 2 line display, 10 programmable keys, handsfree dialing.
b) Material
ELEC-9.4.13 | 1 | Digital Key Telephone with 2 line display, 10 programmable keys, handsfree dialing. | 1 | No | 1 | No | 13752 | 13752
|  | Cost of Material for 1 No | [5 empty] | 13752
|  | Add Overhead @ 10.615% | [5 empty] | 1459.7748
|  | Cost of Material | [5 empty] | 15211.7748
|  | Rounded off rate | [5 empty] | 15212
10pair Telephone distribution box
Data
SD-NA |  | Supply and installation of 10pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement.
b) Material
Elec-9.1.2-b | 1 | "Supply of 20pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement. | 1 | No | 1 | No | 851 | 851
|  | Cost of Material for 1 No | [5 empty] | 851
Provisional rate | 2 | a)Labour for installation (derived from agreement approved rate EE(Gl) Agt No.82/2025-26 Dt.09.07.2019 | 1 | Job | 1 | Job | 90 | 90
|  | Total Cost of Material + Labour Charges | [5 empty] | 941
|  | Add Overhead @ 10.615% | [5 empty] | 99.8871
|  | Cost of Material | [5 empty] | 1040.8872
|  | Rounded off rate | [5 empty] | 1041
Caller ID Pushbutton Telephone instruments
Data
Approved rate |  | Supply and installation of Caller ID Pushbutton Telephone instruments Make: Beetel
EE(Gl) Agreement rate |  | b) Material
| 1 | Supply and installation of Caller ID Pushbutton Telephone instruments Make: Beetel (Approved rate from MRC Qtrs) | 1 | No | 1 | No | 637 | 637
|  | Cost of Material for 1 No | [5 empty] | 637
2Port Line Protection Unit
Data
Approved rate |  | Supply and installation of 2Port Line Protection Unit of Make: Crystla
EE(Gl) Agreement rate |  | b) Material
|  | Supply and installation of 2Port Line Protection Unit of Make: Crystla (Approved rate from MRC Qtrs) | 1 | No | 1 | No | 1200 | 1200
|  | Cost of Material for 1 No | [5 empty] | 1200
6U net work rack
Data
Finished item |  | Supply and installation of 6U 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilevershelf etc., complete. Makes : Vallrack (Legrand) / Netrack.
b) Material
ELEC-9.1.16 a | 1 | Supply and installation of 6U 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK 08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilevershelf etc., complete. Makes : Vallrack (Legrand) / Netrack. | 1 | No | 1 | No | 7392 | 7392
|  | Add OH @10.615% | [5 empty] | 784.6608
|  | Cost of Material for 1 No | [5 empty] | 8176.6608
|  | Rounded off rate | [5 empty] | 8177
Modular telephone Jack with connector
Data
24-25 RSD 2.1.4 |  | supply and fixing of Modular telephone Jack with connector on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : :Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 775 | 25.575
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 650 | 21.45
|  | Labour for 1 Point | [5 empty] | 47.025
|  | Add GHMC allowance @40% | [5 empty] | 18.81
|  | Labour Sub total | [5 empty] | 65.835
b) Material
ELEC-1.3.1.a | 3 | Supply of 1 or 2 Module box | 1 | Nos | 1 | No | 84 | 84
ELEC-1.3.4.a | 4 | Supply of 1 or 2 Modular Cover Frame.
|  | Makes : Legrand Lyncus / GM Four Five / Goldmedal Curve / Million Milltech / Anchor Roma Plus | 1 | Nos | 1 | No | 75 | 75
ELEC-1.9.2.o | 5 | Supply of Modular socket type Telephone jack with Connector. Legrand Lyncus / GM Four Five / Million Milltech / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 95 | 95
|  | Total material cost | [5 empty] | 254
|  | Total Material and Labour charges for 1 no | [5 empty] | 319.835
|  | Add OH @10.615% | [5 empty] | 33.9505
|  | Cost of Material for 1 No | [5 empty] | 353.7855
|  | Rounded off rate | [5 empty] | 354
5 KVA UPS
Data
Supply, Transportation and installation of 5 KVA, 192 / 240V DC true on line UPS system IGBT technology pure sine wave out put, with double conversion with auto and manual static by pass switch single phase input / Single phase output. Makes: Numeric / Emerson / Fuji Electric
ELEC-13.1.2.d | 1 | Supply, Transportation and installation of 5 KVA, 192 / 240V DC true on line UPS system IGBT technology pure sine wave out put, with double conversion with auto and manual static by pass switch single phase input / Single phase output. Makes: Numeric / Emerson / Fuji Electric | 1 | Each | 1 | Each | 67795 | 67795
|  | Add Overhead @ 10.615% | [5 empty] | 7196.4393
|  | Sub total 1 | [5 empty] | 74991.4392
|  | Rounded off rate | [5 empty] | 74991
BATTERY
Data
Supply and fixing of 12V 26 AH SMF battery including wire leads. Makes : Quanta / Racket / Exide / Amaron.
ELEC-13.2..2.a | 3 | Supply and fixing of 12V 26 AH SMF battery including wire leads. Makes : Quanta / Racket / Exide / Amaron. | 1 | Nos | 1 | No | 4301 | 4301
|  | Cost of Material | [5 empty] | 4301
|  | Add Overhead @ 10.615% | [5 empty] | 456.5512
|  | Total Rate | [5 empty] | 4757.5512
|  | Rounded off rate | [5 empty] | 4758
BATTERY RACK
Data
Supply and providing of UPS cum battery rack 11 to 20 batteries
ELEC-13.2..1.c | 3 | Supply and providing of UPS cum battery rack 11 to 20 batteries | 1 | Nos | 1 | No | 5060 | 5060
|  | Cost of Material | [5 empty] | 5060
|  | Add Overhead @ 10.615% | [5 empty] | 537.119
|  | Total Rate | [5 empty] | 5597.119
|  | Rounded off rate | [5 empty] | 5597
DG SET
Data
ELEC 12.1.1 f |  | Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 40 KVA/ 32 KW out put continuous rating directly coupled Engine, Alternator and radiator with guard and mounted on a common base frame of Robust construction and complete with standard control panel having IP-52 protection, anti vibration mounts of reputed make, Acoustic Enclosure as per CPCB norms IV, sound absorbing material to restrict sound level up to 75 dB up to 1 mtr distance and etc as per the following specifications mentioned. | 1 | Nos | 1 | No | 613180 | 613180
A. Alternator : Kirloskar / Stamford / Crompton Greaves / Leroy Somer make. The alternator of the output rating shall be 3 Phase, 415V, 50Hz, Ac , 0.8 P.F. lagging at 1500 RPM. The alternator is self excited, self regulated, and shall confirm to IS: 13364 of 1992 with regulation of +5% from no load to full load. degree of protections shall be IP23.
B.Diesel Engine : Kirloskar / Cummins / Mahindra & Mahindra / Greaves Cotton / Eicher / Ashok Leyland Diesel Engine start, developing suitable BHP output at 1500 RPM with mechanical / electronic governing so as to enable the alternator to give 40 KVA continuous output at 0.8 P.F. lagging at NTP conditions. The diesel engine shall be capable of providing 10% O/L for 1 Hr for every 11 Hrs of continuous running at full load. The engine with 1st filling of oil and Diesel etc. 01. Exhaust pipe of required size as per the standards. 02. Diesel tank suitable for 8 to 12 Hours running capacity. 03. Residential Silencer. 04. SMF Batteries with leads as per the Manufacturer standards
40 KVA, 3 Phase, 415, 50 Hz, 56 BHP, water cooled multy cylinder diesel generator set with alternator of 40 KVA output continious rating at 0.8 p.f. Batteries.
|  | Cost of Material | [5 empty] | 613180
|  | Add Overhead @ 10.615% | [5 empty] | 65089.057
|  | Total Rate | [5 empty] | 678269.057
|  | Rounded off rate | [5 empty] | 678269
Changeover with Enclosure
Data
Replacement of old u/s with new Supply and fixing of 125 A 4 Pole Change Over Switch on Load with open Execution with enclosure Makes : Socomec / LK
Material:-
ELEC 2.2.1 B |  | Supply of 125 A 4 Pole Change Over Switch on Load with open Execution. Makes : Socomec / LK | 1 | Nos | 1 | No | 11850 | 11850
EB Metering Equipment:-
ELEC-8.17.6-b |  | Supply and erection of RYB LED indicator lamps on the existing box / panel board of Makes :LK / / SALZAR / HPL / Siemens | 3 | Nos | 1 | No | 165 | 495
ELEC-8.17.1.A |  | Supply and erection of 0-500V Digital Volt meter on exisiting panel board including connections etc., complete. MAKES :CONZERVE / ELMEASURE / LK / SEIMENS. | 1 | Nos | 1 | No | 2425 | 2425
ELEC-8.17.2.A |  | Supply and erection of 0-100 / 200 / 400 / 600 /1000 Digital Ammeter of size 96x96mm on existing panel board including connections etc., complete.MAKES : CONZERVE / ELMEASURE / LK / SEIMENS. | 1 | Nos | 1 | No | 2425 | 2425
ELEC-8.17.6-A |  | Supply and erection of Selector switch for Voltmeter / Ammeter on the existing panel including connections etc., complete. -Makes : LK / / SALZAR / HPL / Siemens | 2 | Nos | 1 | No | 215 | 430
ELEC-8.17.7 |  | Supply and erection of LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing panel including connections etc., complete. MAKE : KAPPA | 3 | Nos | 1 | No | 530 | 1590
|  | SUB-TOTAL 1 | [5 empty] | 19215
|  | Fabrication of cubical panel board made out of 14 gauge out frame and 16 gauge partitions and base channel, bus bars (0.8 A / sq mm) etc., complete with locks, door lopp earthing etc., @ 35% |  |  |  |  | 6725.25 | 6725.25
|  | Sub Total | [5 empty] | 25940.25
|  | Add Overhead @ 10.6150% | [5 empty] | 2753.5575
|  | Total Rate | [5 empty] | 28693.8075
|  | Rounded off rate | [5 empty] | 28694
12 " Metallic Exhaust Fan for Kitchen
Data
24-25 RSD 9.7.2+RSD 9.7.36 |  | Replacement of old u/s with new Supply of 12" (300mm +/ - 5%)Light duty exhaust fan with metal blades etc complete for ante rooms / individual toilets. Makes : Crompton / Havells VentilairDSP / Orient hill air.
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.25 | day | 1 | day | 775 | 193.75
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.25 | day | 1 | day | 650 | 162.5
|  | Labour for 1 No | [5 empty] | 356.25
|  | Add GHMC Allowance @40% | [5 empty] | 142.5
|  | Labour subtotal | [5 empty] | 498.75
| 3 | Sundries such as Bolt, Nuts, twin core wire if necessary etc. |  |  |  |  | 15 | 15
|  | Cost of Material for fixing fan | [5 empty] | 15
b) Material
ELEC-5.1.11 b | 4 | Supply of 12" (300mm +/ - 5%)Light duty exhaust fan with metal blades etc complete for ante rooms / individual toilets. Makes : Crompton / Havells VentilairDSP / Orient hill air. | 1 | No | 1 | No | 1817 | 1817
|  | Transportation Charges on Unit Cost @1% |  |  |  |  | 1% | 18.17
|  | Cost of Material for 1 No | [5 empty] | 1850.17
|  | Total Cost of Material + Labour Charges | [5 empty] | 2348.92
|  | Add Overhead @ 10.615% | [5 empty] | 249.3379
|  | Total Rate | [5 empty] | 2598.2579
|  | Rounded off rate | [5 empty] | 2598
6 " Shutter type Exhaust Fan for Bathrooms
Data
24-25 RSD 9.7.2+RSD 9.7.36 |  | Replacement of old u/s with new Supply of 6" (150mm)Ventilating exhaust fan with shutters etc complete for living rooms / office roomsMakes : Crompton / Havells Ventilair DX / Orient
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.25 | day | 1 | day | 775 | 193.75
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 0.25 | day | 1 | day | 650 | 162.5
|  | Labour for 1 No | [5 empty] | 356.25
|  | Add GHMC Allowance @40% | [5 empty] | 142.5
|  | Labour subtotal | [5 empty] | 498.75
| 3 | Sundries such as Bolt, Nuts, twin core wire if necessary etc. |  |  |  |  | 15 | 15
|  | Cost of Material for fixing fan | [5 empty] | 15
b) Material
ELEC-5.1.12 a | 4 | Supply of 6" (150mm)Ventilating exhaust fan with shutters etc complete for living rooms / office roomsMakes : Crompton / Havells Ventilair DX / Orient | 1 | No | 1 | No | 1487 | 1487
|  | Transportation Charges on Unit Cost @1% |  |  |  |  | 1% | 14.87
|  | Cost of Material for 1 No | [5 empty] | 1516.87
|  | Total Cost of Material + Labour Charges | [5 empty] | 2015.62
|  | Add Overhead @ 10.615% | [5 empty] | 213.9581
|  | Total Rate | [5 empty] | 2229.5781
|  | Rounded off rate | [5 empty] | 2230
WPTC 10 Sq.mm
Data
24-25- RSD 3.1.5 |  | Rewiring with Supply of 10 Sq.mm WPTC (Weather Proof Twin Core) ISI mark Alluminium Wire. Makes : Polycab / V- Guard / HPL/ Finecab / Pawancab
a) Labour charges :
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 775 | 775
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 3 | day | 1 | day | 650 | 1950
| 3 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 650 | 650
|  | Labour for 100 Mtr | [5 empty] | 3375
|  | Labour for 1 Mtr | [5 empty] | 33.75
|  | Add GHMC Allowance @40% | [5 empty] | 13.5
|  | Labour subtotal | [5 empty] | 47.25
b) Material
ELEC-1.6.2-B | 4 | Supply of 10 Sq.mm WPTC (Weather Proof Twin Core) ISI mark Alluminium Wire. Makes : Polycab / V- Guard / HPL/ Finecab / Pawancab | 100 | Mtrs | 100 | Mtrs | 4956 | 4956
|  | Cost of Material for 100 Metres | [5 empty] | 4956
|  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 49.56
|  | Total Cost of Material + Labour Charges | [5 empty] | 96.81
|  | Add Overhead @ 10.615% | [5 empty] | 10.2764
|  | Total Rate | [5 empty] | 107.0864
|  | Rounded off rate | [5 empty] | 107
10W LED Bulk head fitting
Data
SD-N.A |  | Replacement of old u/s with new Supply and transportation of 10W LED Bulk head fitting with milky diffuser heat sink integrated with housing with all accessories etc complete with 5 years warranty warranty.LUMINAIRE MAKE : PHILIPS / CROMPTON LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs.
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.04 | day | 1 | day | 775 | 31
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.04 | day | 1 | day | 650 | 26
|  | Labour | [5 empty] | 57
|  | Add GHMC Allowance @40% | [5 empty] | 22.8
|  | Labour subtotal | [5 empty] | 79.8
b) Material
Cost of Material for fixing luminaire
ELEC-3.5.8 | 7 | Supply and transportation of 10W LED Bulk head fitting with milky diffuser heat sink integrated with housing with all accessories etc complete with 5 years warranty warranty.LUMINAIRE MAKE : PHILIPS / CROMPTON LED MAKE : Philips Lumileds / Cree / Nichia / Osram / Samsung / LG LEDs. | 1 | No | 1 | No | 387.1 | 387.1
|  | Cost of Material | [5 empty] | 387.1
|  | Total Cost of Material + Labour Charges | [5 empty] | 466.9
|  | Add Overhead @ 10.615% | [5 empty] | 49.5614
|  | Total Rate | [5 empty] | 516.4614
|  | Rounded off rate | [5 empty] | 516
6.0 Sqmm 4 Core
Data
Rewiring with Supply and Laying of 6.0 Sqmm 4 CoreP PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:2010 includingalltransportation charges etc complete. Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 775 | 387.5
| 2 | Semi skilled Electrician / Helper. SOR-2025-26 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 650 | 1300
|  | Labour Charges for 100 Mtrs | [5 empty] | 1687.5
|  | Labour Charges for 1 Mtr | [5 empty] | 16.875
|  | Add GHMC Allowance @40% | [5 empty] | 6.75
|  | Labour Sub total | [5 empty] | 23.625
b) Material
ELEC-1.5.5-v | 3 | Supply of 6.0 Sqmm 4 CoreP PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:2010 includingalltransportation charges etc complete. Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI / Gloster / V-Guard / Finecab / SPM / Gemini / Unistar / Windsor / Payal / Fortune Arrt / Avocab / Pawancab / Nakoda / HPL / Sudhakar / Bonton / Rajnigandha | 1 | Mtr | 1 | Mtr | 429 | 429
|  | Cost of Material | [5 empty] | 429
|  | Total Material and Labour charges for 1 mts | [5 empty] | 452.625
|  | Add Overhead @ 10.615% | [5 empty] | 48.0461
|  | Cost of Material | [5 empty] | 500.6711
|  | Rounded off rate | [5 empty] | 501
1.50 HP Monoblock
Data
Finished item |  | Repalcement of u/s with new Supply and Transportation of 1.5 HP (32x25mm) Single phase ISI Mono block CI body motor pumpset including starter and all labour charges. Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon
a) Labour charges
| 1 | Skilled Electrician. SOR-2025-26 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 775 | 387.5
| 2 | Helper. SOR-2025-26 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 650 | 325
|  | Labour | [5 empty] | 712.5
|  | Add GHMC Allowance @40% | [5 empty] | 285
|  | Labour subtotal | [5 empty] | 997.5
b) Material
ELEC-5.6.1-d | 1 | Supply and Transportation of 1.5 HP (32x25mm) Single phase ISI Mono block CI body motor pumpset. Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon | 1 | Nos | 1 | Nos | 21000 | 21000
|  | Supply & Fixing of D.O.L Starter 250V, Single phase, 50Hz. With Sheet Steel enclouser comprising of contactor with bi-metalic relay with neceSheet Steelary push buttons, etc., complete suitable upto 3 H.P Makes: Siemens / LK / BCH | 1 | Nos | 1 | Nos | 2400 | 2400
|  | Cost of Material | [5 empty] | 23400
|  | Add Overhead @ 10.615% | [5 empty] | 2483.91
|  | Total | [5 empty] | 25883.91
|  | Rounded of Rate | [5 empty] | 25884
LED Strip 28W
Data
24-25 RSD 8.1.2 |  | Replacement of old damaged by new supply and fixing of LED Strip 28W 5mtrs Lenth philips as desired by the department and as per IS,inlcuding all labour charges etc., complete
|  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
| 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.05 | day | 1 | day | 735 | 36.75
| 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.05 | day | 1 | day | 615 | 30.75
|  | Labour | [5 empty] | 67.5
|  | Add GHMC Allowance @40% | [5 empty] | 27
|  | Labour subtotal | [5 empty] | 94.5
b) Material
AR | 3 | Supply of LED Strp 28W 5mtrs Lenth of make philips (Approved rate from MRC Qtrs) | 5 | Mtrs | 5 | Mtrs | 1375 | 1375
|  | Cost of Material | [5 empty] | 1375
|  | Total Cost of Material + Labour Charges | [5 empty] | 1469.5
|  | Rounded of Rate | [5 empty] | 1470
Casing And Capping 25 mm
Data
24-25 RSD 1.3.2 |  | Replacement of old damaged by new supply of 25mm x 12 mm and thickness 1.2 mm width and height Casing and Caping with all accessories such as Ts, Bends, Elbows etc., complete for finished item of work. Makes : Modi with ISI or its equivalent make as approved by the department
Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC
|  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
| 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 735 | 735
| 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615 | 615
| 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615 | 615
|  | Labour Rate Per 100 Rm | [5 empty] | 1965
|  | Labour Rate for 1 Mtr | [5 empty] | 19.65
|  | Add GHMC Allowance @40% | [5 empty] | 7.86
|  | Labour subtotal | [5 empty] | 27.51
b) Material
Elec 10.1.2 | 4 | Rawl Plugs. (SOR-2024-25- ELEC-10.1.2) | 200 | Nos | 100 | Nos | 45 | 90
Elec 1.4.4-d | 5 | Supply of No.8 Screws of 35/38mm. (SOR-2024-25 ELEC-1.4.4-d) | 200 | Nos | 100 | Nos | 135 | 270
Elec 1.2.5 b | 10 | Replacement of old damaged by new supply of 25mm x 12 mm and thickness 1.2 mm width and height Casing and Caping with all accessories such as Ts, Bends, Elbows etc., complete for finished item of work. Makes : Modi with ISI or its equivalent make as approved by the department | 100 | Mtr | 1 | Mtr | 32 | 3200
|  | Material Rate for 100 Mtrs | [5 empty] | 3560
|  | Material Rate for 1 Mtr | [5 empty] | 35.6
|  | Total Cost of Material + Labour Charges | [5 empty] | 63.11
|  | Add Overhead @ 10.615% | [5 empty] | 6.6991
|  | Total Rate | [5 empty] | 69.8091
|  | Rounded off rate | [5 empty] | 70
LT Panel (1 No I/C 400A MCCB & 10 Nos O/G 125 A MCCB)
Data
Replacement of old u/s with new Supply, Fabrication,transpotation, Erection, testing and Commissioing of conventional LT Panel suitable for 415V, 3 Phases, 4wire, 50Hz AC Supply system fabricated in comparmentalized design with CRCA sheet steel of 1.6mm thick from frame work and covers, 2mm CRCA thick for gland plate including cleaning and finishing complete with seven tank process for powder coating approved shade having busbar 500A capacity equal in size for phase and neutral, extensible type FP alluminum alloy busbars of high conductivity, DMC/SMC/Busbar supports with shortcircuit withstand capacity of 35/36KA for 1 sec, preventing access to live parts as per type tested Replacement of old u/s with new bottom based channel of suitable size, fabrication done in transportable section, entire panel shall have a common suitable GI earth continuous bar at rear side with 2Nos earth stud, solid connections from main Busbar to switchgears with required size of alumium busbars with control wiring, etc complete with providing following switchgears
Incoming
(ELEC-2.8.1-j) | 1 | Supply of 400A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35 / 36 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V | 1 | Nos. | 41470 | 1 | Each | 41470
(ELEC-2.11.3-h) | 2 | ﻿Supply and Transportation of spreader links of 400A 4 pole | 1 | Set | 1700 | 1 | Each | 1700
(ELEC-2.11.4-c) | 3 | ﻿Supply and Transportation of Rotary Handles of 400A | 1 | Set | 2600 | 1 | Each | 2600
ELEC- 8.17.1 - a | 4 | Supply and erection of 0-500V volt Digital meter of size 96 x 96mm on exisiting box / panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS / . | 1 | Nos. | 2425 | 1 | Each | 2425
ELEC- 8.17.2 - a | 5 | Supply and erection of 0- 400A Digital Ammeter of size 96 x 96mm on existing box / panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS / . | 1 | Nos. | 2425 | 1 | Each | 2425
ELEC-8.17.6-c | 6 | Supply and erection of Push buttons on the existing panel board. Makes : LK (L&T) / C&S / SALZAR / / Siemens | 2 | Nos. | 90 | 1 | Each | 180
ELEC-8.17.6-b | 7 | Supply and erection of LED Phase indication lamps on the existing panel board Makes : LK (L&T) / C&S / SALZAR / / Siemens | 6 | Nos. | 165 | 1 | Each | 990
ELEC- 8.17.7 | 8 | Supply and erection of LT current transformer with bar primary 400 / 5A ratio in the existing panel including connections etc., complete. MAKE : KAPPA | 3 | Nos. | 530 | 1 | Each | 1590
(ELEC-2.14.1-a) | 9 | ﻿Supply of 6A SPMCB 10 kA, C/D Curve ISI Mark. Makes :Legrand-DX3 / Schneider-Acti9 / Siemens / LK Exora / BCH / Havells Stadx | 4 | Nos. | 325 | 1 | Each | 1300
Out Going
(ELEC-2.8.1-c) | 10 | Supply of 125A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V | 10 | Nos. | 11380 | 1 | Each | 113800
(ELEC-2.11.3-a) | 11 | ﻿Supply and Transportation of spreader links of 125A 3 pole | 10 | Set | 270 | 1 | Each | 2700
(ELEC-2.11.4-a) | 12 | ﻿Supply and Transportation of Rotary Handles upto 160A | 10 | Set | 1450 | 1 | Each | 14500
| 13 | Out Going: Powers section
(ELEC-2.8.1-a) | 14 | Sub Incomer: Supply of 63A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V | 10 | Nos. | 9600 | 1 | Each | 96000
(ELEC-2.14.1-a) | 15 | ﻿Supply of 32A SPMCB 10 kA, C/D Curve ISI Mark. Makes :Legrand-DX3 / Schneider-Acti9 / Siemens / LK Exora / BCH / Havells Stadx ( 3 set of 6 nos 32A SPMCB * 2 sets = 3*6*2=36 nos) | 2 | Nos. | 340 | 1 | Each | 680
| 16 | Out Going: lighting section
(ELEC-2.8.1-a) | 17 | Sub Incomer: Supply of 63A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V | 1 | Nos. | 9600 | 1 | Each | 9600
(ELEC-2.14.1-a) | 18 | ﻿Supply of 16A SPMCB 10 kA, C/D Curve ISI Mark. Makes :Legrand-DX3 / Schneider-Acti9 / Siemens / LK Exora / BCH / Havells Stadx ( 3 set of 6 nos 32A SPMCB * 2 sets = 3*6*2=36 nos) | 2 | Nos. | 325 | 1 | Each | 650
|  | Sub Total - I | [5 empty] | 292610
|  | Fabrication of Cubical Panel board made out of 14 guage outframe &16 guage partitions and base channel, bus bars (0.8A/sqmm) etc complete with locks, door loop earthing etc (Sub total - I *30%) | [5 empty] | 87783
|  | Sub Total - II | [5 empty] | 380393
|  | Add OH&CP@10.615% | [5 empty] | 31060.5515
|  | Total: | [5 empty] | 411453.5515
|  | Rounded off to nearest Ten Rupees | [5 empty] | 411450
Outdoor type LT Panel ( 1 No 125 A I/C & 18 Nos 63 A MCBs O/G)
Data
Replacement of old u/s with new Supply, Fabrication,transpotation, Erection, testing and Commissioing of conventional LT Panel suitable for 415V, 3 Phases, 4wire, 50Hz AC Supply system fabricated in comparmentalized design with CRCA sheet steel of 1.6mm thick from frame work and covers, 2mm CRCA thick for gland plate including cleaning and finishing complete with seven tank process for powder coating approved shade having busbar 150A capacity equal in size for phase and neutral, extensible type FP alluminum alloy busbars of high conductivity, DMC/SMC/Busbar supports with shortcircuit withstand capacity of 35/36KA for 1 sec, preventing access to live parts as per type tested Replacement of old u/s with new bottom based channel of suitable size, fabrication done in transportable section, entire panel shall have a common suitable GI earth continuous bar at rear side with 2Nos earth stud, solid connections from main Busbar to switchgears with required size of alumium busbars with control wiring, etc complete with providing following switchgears
Incoming
(ELEC-2.8.1-d) | 1 | Supply of 125A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V | 1 | Nos. | 13770 | 1 | Each | 13770
(ELEC-2.11.3-b) | 2 | ﻿Supply and Transportation of spreader links of 125A 4 pole | 1 | Set | 360 | 1 | Each | 360
(ELEC-2.11.4-a) | 3 | ﻿Supply and Transportation of Rotary Handles up to 160A | 1 | Set | 1450 | 1 | Each | 1450
ELEC- 8.17.1 - a | 4 | Supply and erection of 0-500V volt Digital meter of size 96 x 96mm on exisiting box / panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS / . | 1 | Nos | 2425 | 1 | Each | 2425
ELEC- 8.17.2 - a | 5 | Supply and erection of 0- 400A Digital Ammeter of size 96 x 96mm on existing box / panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS / . | 1 | Nos | 2425 | 1 | Each | 2425
ELEC-8.17.6-c | 6 | Supply and erection of Push buttons on the existing panel board. Makes : LK (L&T) / C&S / SALZAR / / Siemens | 2 | Nos | 90 | 1 | Each | 180
ELEC-8.17.6-b | 7 | Supply and erection of LED Phase indication lamps on the existing panel board Makes : LK (L&T) / C&S / SALZAR / / Siemens | 6 | Nos | 165 | 1 | Each | 990
ELEC- 8.17.7 | 8 | Supply and erection of LT current transformer with bar primary 400 / 5A ratio in the existing panel including connections etc., complete. MAKE : KAPPA | 3 | Nos | 530 | 1 | Each | 1590
(ELEC-2.14.1-a) | 9 | ﻿Supply of 6A SPMCB 10 kA, C/D Curve ISI Mark. Makes :Legrand-DX3 / Schneider-Acti9 / Siemens / LK Exora / BCH / Havells Stadx | 4 | Nos. | 340 | 1 | Each | 1360
Out Going
(ELEC-2.14.1-f) | 10 | Sub Incomer: ﻿Supply of 50-63A DP MCB 10 kA, C/D Curve ISI Mark. Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / LK (L&T) Exora | 18 | Nos | 1700 | 1 | Each | 30600
(ELEC-2.16.8-c) | 11 | ﻿Supply of 32ATP Plug and Socket with SS enclosure. Makes : Legrand / Schneider / Siemens / LK(L&T) | 18 | Nos | 3530 | 1 | Each | 63540
|  | Sub Total - I | [5 empty] | 118690
|  | Fabrication of Cubical Panel board made out of 14 guage outframe &16 guage partitions and base channel, bus bars (0.8A/sqmm) etc complete with locks, door loop earthing, etc (Sub total - I *30%) | [5 empty] | 35607
|  | Sub Total - II | [5 empty] | 154297
|  | Add OH&CP@10.615% | [5 empty] | 12598.9435
|  | Total: | [5 empty] | 166895.9435
|  | Rounded off to nearest Ten Rupees | [5 empty] | 166900

## Groups
Item Name | Group | Prefix | Unit
1.5 TR Split AC's | HVAC | Replacement of old damaged u/s by new | Nos
1.50 HP Borewell Pumpset | Motors & Pumpsets | Replacement of old damaged u/s by new | Nos
1.50 HP Monoblock | Motors & Pumpsets | Replacement of old damaged u/s by new | Nos
1.8/2.0 TR Split AC's | HVAC | Replacement of old damaged u/s by new | Nos
10pair Telephone distribution box | Telephone System | Replacement of old damaged u/s by new | Nos
10W LED Bulk head fitting | Internal Lighting | Replacement of old damaged u/s by new | Nos
12 " Metallic Exhaust Fan for Kitchen | Fans & Exhaust fans | Replacement of old damaged u/s by new | Nos
1200mm length LED light | Fans & Exhaust fans | Replacement of old damaged u/s by new | Nos
12Module (6A Sockets & -6A Switches - Four Nos) | Switch Boards & Accessories | Replacement of old damaged u/s by new | Nos
15W LED Slimline Panel Light | Internal Lighting | Replacement of old damaged u/s by new | Nos
15W LED Surface Mounted Down Light | Internal Lighting | Replacement of old damaged u/s by new | Nos
25 Sqmm Cable | U.G Cabling | Replacement of old damaged u/s by new | Mtrs
2Port Line Protection Unit | Telephone System | Replacement of old damaged u/s by new | Nos
3 Core x 2.5 Sqmm Armoured Cable | U.G Cabling | Replacement of old damaged u/s by new | Mtrs
3 feet length moulded patch cord. | Telephone System | Replacement of old damaged u/s by new | Nos
35 Sqmm Cable | U.G Cabling | Replacement of old damaged u/s by new | Mtrs
4 Core x 4 Sqmm Armoured Cable | U.G Cabling | Replacement of old damaged u/s by new | Mtrs
4.0 Sqmm 4 Core | Sheathed Cables | Replacement of old damaged u/s by new | Mtrs
4Module 3W LED Foot lamp | Internal Lighting | Replacement of old damaged u/s by new | Nos
4Way TPN DB | DBs & Equipment | Replacement of old damaged u/s by new | Mtrs
50 Sqmm 3.5 core Cable | U.G Cabling | Replacement of old damaged u/s by new | Mtrs
6 " Shutter type Exhaust Fan for Bathrooms | Fans & Exhaust fans | Replacement of old damaged u/s by new | Nos
6.0 Sqmm 4 Core | Sheathed Cables | Replacement of old damaged u/s by new | Mtrs
6Module (6A Sockets & -6A Switches - Two Nos) | Switch Boards & Accessories | Replacement of old damaged u/s by new | Nos
6U net work rack | LAN system | Replacement of old damaged u/s by new | Nos
8 Port D-Link | LAN system | Replacement of old damaged u/s by new | Nos
8 SWG GI Wire | Earthing | Replacement of old damaged u/s by new | Mtrs
8 Way VTPN DB | DBs & Equipment | Replacement of old damaged u/s by new | Nos
8Module (6A Sockets & -6A Switches - Three Nos) | Switch Boards & Accessories | Replacement of old damaged u/s by new | Nos
8way SPN DB | DBs & Equipment | Replacement of old damaged u/s by new | Nos
BATTERY | UPS | Replacement of old damaged u/s by new | Nos
BATTERY RACK | UPS | Replacement of old damaged u/s by new | Nos
Booster Pump | Motors & Pumpsets | Replacement of old damaged u/s by new | Nos
Caller ID Pushbutton Telephone instruments | Telephone System | Replacement of old damaged u/s by new | Nos
Casing And Capping 25 mm | Conduiting | Replacement of old damaged u/s by new | Mtrs
Cat 6 Cable | LAN system | Replacement of old damaged u/s by new | Mtrs
Ceiling Fans | Fans & Exhaust fans | Replacement of old damaged u/s by new | Nos
Changeover with Enclosure | Panel Boards | Replacement of old damaged u/s by new | Nos
Common Switch Board | Switch Boards & Accessories | Replacement of old damaged u/s by new | Nos
Copper Pipe | HVAC | Replacement of old damaged u/s by new | Mtrs
Core Cuttting | HVAC | Replacement of old damaged u/s by new | Nos
CPVC Pipe | HVAC | Replacement of old damaged u/s by new | Mtrs
DG SET | Diesel Generator | Replacement of old damaged u/s by new | Nos
Digital Key Telephone with 2 line display | Telephone System | Replacement of old damaged u/s by new | Nos
Ding Dong Bell | Bells | Replacement of old damaged u/s by new | Nos
Earthwork excavation of UG Cable | Earthing | Replacement of old damaged u/s by new | Mtrs
EPABX System | Telephone System | Replacement of old damaged u/s by new | Nos
Exhaust Fan | Fans & Exhaust fans | Replacement of old damaged u/s by new | Nos
Fan and Exhaust Fan Points : Residential Building | Points | Re- | Pts
Fan and Exhaust Fan Points : Non-Residential Building | Points | Re- | Pts
Flood Light | External Lighting | Replacement of old damaged u/s by new | Nos
GI Strip | Earthing | Replacement of old damaged u/s by new | Mtrs
Independent earthing | Earthing | Replacement of old damaged u/s by new | Nos
Information Outlets | LAN system | Replacement of old damaged u/s by new | Nos
Labour charges for dressing and rectification of cables | Miscelleneous | Replacement of old damaged u/s by new | Jobs
Laying of 35 & 25 Sqmm Cable | U.G Cabling |  | Mtrs
Laying of 50 Sqmm Cable | U.G Cabling |  | Mtrs
LED Strip 28W | Internal Lighting | Replacement of old damaged u/s by new | Nos
Light & Bell Points : Residential Building | Points | Re- | Pts
Light & Bell Points : Non-Residential Building | Points | Re- | Pts
LT Panel (1 No I/C 400A MCCB & 10 Nos O/G 125 A MCCB) | Panel Boards | Replacement of old damaged u/s by new | Nos
Mirror Lights | Internal Lighting | Replacement of old damaged u/s by new | Nos
Modular co-Axial socket type TV | Switch Boards & Accessories | Replacement of old damaged u/s by new | Nos
Modular telephone Jack with connector | Telephone System | Replacement of old damaged u/s by new | Nos
Outdoor type LT Panel ( 1 No 125 A I/C & 18 Nos 63 A MCBs O/G) | Panel Boards | Replacement of old damaged u/s by new | Nos
Patch panel | LAN system | Replacement of old damaged u/s by new | Nos
Power Plug | Switch Boards & Accessories | Replacement of old damaged u/s by new | Nos
Power Plug Two Nos | Switch Boards & Accessories | Replacement of old damaged u/s by new | Nos
6 U Wall Rack | LAN system | Replacement of old damaged u/s by new | Nos
Rg-6 Cable | Telephone System | Replacement of old damaged u/s by new | Mtrs
Run of 1 of 1.50 Sq.mm | Run of Mains | Rewiring with | Mtrs
Run of 3 of 2.5 Sq.mm Copper Cable | Run of Mains | Rewiring with | Mtrs
Run of 3 of 4.0 Sq.mm Copper Cable | Run of Mains | Rewiring with | Mtrs
Run of 5 of 6.0 Sq.mm Copper Cable | Run of Mains | Rewiring with | Mtrs
Starter for Motors | Motors & Pumpsets | Replacement of old damaged u/s by new | Nos
Stepped Electronic Regulator | Fans & Exhaust fans | Replacement of old damaged u/s by new | Nos
Surface PVC Pipe | Conduiting | Replacement of old damaged u/s by new | Mtrs
Thermo Plastic Box with Switch gear | External Lighting | Replacement of old damaged u/s by new | Nos
5 KVA UPS | UPS | Replacement of old damaged u/s by new | Nos
25 Ltrs Water Heater (Geysers) | Water Heaters | Replacement of old damaged u/s by new | Nos
WPTC 10 Sq.mm | Sheathed Cables | Replacement of old damaged u/s by new | Mtrs