## Master Datas
| Item |  | Description | Quantity |  | Unit |  | Rate | Amount | Concealed PVC Pipe
|  |  | Concealed PVC Pipe | [6 empty] | Surface PVC Pipe
|  |  | Data-1 | [6 empty] | Light & Bell Points in RB
1 | 24-25-RSD 1.4.1(b) |  | Supply and laying of ISI 25mm outer dia medium grade with IS:9537 part 3 rigidPVC pipe concealed in wall with PVC / Metallic junction boxes, accessories including masonary work for light, fan and separate plug point including chisseling brick work, engaging skilled mason for fine wall cement plastering & all labour charges etc., complete for Modular concealed wiring. Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC | [6 empty] | Fan and Exhaust Fan Points in RB
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount | Common Switch Board
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 735 |  | Power Plug
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615 |  | Power Plug Two Nos
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615 |  | 6Module (6A Sockets & -6A Switches - Two Nos)
|  | 4 | Mason Cl- I / Brick layer Cl- I SOR-2024-25 Sl No 11 of skilled Labour rates. | 2 | day | 1 | day | 645 |  | 12Module (6A Sockets & -6A Switches - Four Nos)
|  |  | Labour Rate Per 100 Rm | [6 empty] | 8 Module switch Board (6A Sockets & 6A Switches-3 Nos)
|  |  | Labour Rate for 1 Mtr | [6 empty] | 1200mm length LED light
|  |  | Add GHMC allowance@40% | [6 empty] | 15W LED Slimline Panel Light
|  |  | Labour Sub total | [6 empty] | 36W 2' x2' (600mm x 600mm) slim panel LED
|  |  | b) Material | [6 empty] | Ceiling Fans
| ELEC-10.4.10 | 5 | Cement (ELEC-10.4.10) | 50 | Kg | 1 | Kg | 9 |  | Stepped Electronic Regulator
| ELEC-10.1.4 | 6 | U Nails (ELEC-10.1.4) | 200 | Nos | 100 | Nos | 44 |  | Exhaust Fan
| ELEC-1.2.6 b | 7 | Supply of 25mm PVC Junction Boxes Normal of Makes : Sudhakar / Finolex / Modi / VIP / Precision. (Elec-1.2.6-b) | 12 | Nos | 1 | Nos | 28 |  | Ding Dong Bell
| ELEC-1.2.8 b | 8 | Supply of 25mm dia 1.5mm thick PVC Bends of Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal. (Elec-1.2.8-b) | 12 | Nos | 1 | No | 12 |  | Musical Bell
| ELEC-1.2.2 b | 9 | Supply of ISI 25mm outer dia medium grade, FRLS with IS:9537 part 3 regid PVC pipe of Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC. (Elec-1.2.2-b) | 100 | Mtr | 1 | Mtr | 32 |  | Run of 3 of 2.5 Sq.mm Copper Cable
|  |  | Material Rate for 100 Mtrs | [6 empty] | Run of 3 of 4.0 Sq.mm Copper Cable
|  |  | Material Rate for 1 Mtr | [6 empty] | Run of 5 of 6.0 Sq.mm Copper Cable
|  |  | Total Cost of Material + Labour Charges | [6 empty] | 4Way TPN DB
|  |  | Add Overhead @ 10.615% | [6 empty] | 8Way VTPN DB
|  |  | Total Rate | [6 empty] | Water Heater (Geysers)
|  |  | Rounded off rate | [6 empty] | Water Heater hose pipe
|  |  | Surface PVC Pipe | [6 empty] | Street Light
|  |  | Data 2 | [6 empty] | Bollard
2 | 24-25 RSD 1.3.2 |  | Supply and Fixing of ISI marked 25mm outer dia medium grade with IS:9537 part 3 regid PVC pipe on surface of wall with PVC / Metallic junction boxes fixing on chromium plated metallic base saddles including all required materials with redoing wall fine cement plastering etc., completewith all labour charges for run of mains.(Data No.24-25 SD-1.3.2) | [6 empty] | 3 Core x 2.5 Sqmm Armoured Cable
|  |  | Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC | [6 empty] | Panel Board
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount | 4way SPN DB
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 735 |  | 8way SPN DB
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615 |  | Run of 1 of 1.50 Sq.mm
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615 |  | 70 Sqmm Cable
|  |  | Labour Rate Per 100 Rm | [6 empty] | Laying of 70 Sqmm Cable
|  |  | Labour Rate for 1 Mtr | [6 empty] | Earthwork excavation of UG Cable
|  |  | Add GHMC Allowance @40% | [6 empty] | 50 mm Nominal Bore GI pipe
|  |  | Labour subtotal | [6 empty] | 35 Sqmm Cable
|  |  | b) Material | [6 empty] | 25 Sqmm Cable
| Elec 10.1.2 | 4 | Rawl Plugs. (SOR-2024-25- ELEC-10.1.2) | 200 | Nos | 100 | Nos | 45 |  | Laying of 35 & 25 Sqmm Cable
| Elec 1.4.4-d | 5 | Supply of No.8 Screws of 35/38mm. (SOR-2024-25 ELEC-1.4.4-d) | 200 | Nos | 100 | Nos | 135 |  | Speaker Cable
| Elec 10.4.10 | 6 | Cement. ( SOR 24-25 ELEC-10.4.10 ) | 5 | Kg | 1 | Kg | 9 |  | 4Module 3W LED Foot lamp
| ELEC-1.1.11 b | 7 | Supply of 25mm Saddles with Base. (SOR-2024-25-ELEC-1.1.11-b) | 200 | Nos | 100 | Nos | 290 |  | 3W LED light passolite
| ELEC-1.2.6 b | 8 | Supply of 25mm PVC Junction Boxes Normal of Makes : Sudhakar / Finolex / Modi / VIP / Precision. (Elec-1.2.6-b) | 12 | Nos | 1 | No | 28 |  | LED Strip 28W
| ELEC-1.2.8 b | 9 | Supply of 25mm dia 1.5mm thick PVC Bends of Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal. (Elec-1.2.8-b) | 12 | Nos | 1 | No | 12 |  | 4 Way VTPN DB
| Elec 1.2.2 b | 10 | Supply of ISI 25mm outer dia medium grade, FRLS with IS:9537 part 3 regid PVC pipe of Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC (SOR-2024-25-ELEC-1.2.2-b) | 100 | Mtr | 1 | Mtr | 32 |  | Independent earthing
|  |  | Material Rate for 100 Mtrs | [6 empty] | 8 SWG GI Wire
|  |  | Material Rate for 1 Mtr | [6 empty] | 12Way SPN DB
|  |  | Total Cost of Material + Labour Charges | [6 empty] | Heavy duty long barrel alluminium 70 sq mm lugs
|  |  | Add Overhead @ 10.615% | [6 empty] | Heavy duty long barrel alluminium 35 sq mm lugs
|  |  | Total Rate | [6 empty] | Heavy duty long barrel alluminium 16 sq mm lugs
|  |  | Rounded off rate | [6 empty] | Mirror Lights
|  |  | Light & Bell Points in RB | [6 empty] | Telephone Cable
|  |  | Data-3 | [6 empty] | IP Based digtal Telephone
3 | 24-25-RSD 2.1.2 | 24-25-RSD2.1.2 | Wiring with run of 2 of 1.5 Sq.mm FRLS / HFFR PVC insulated flexible ISI marked copper cable in existing consealed pipe including supply and fixing of 3 Plate Jumbo Ceiling rose of Makes : GM G Home / Gold Medal Olive / Million Zoom / Anchor Penta Cherry / Great white Omega / HPL / Vimal / CPL make ,10A ISI marked Modular type switch with cover frame and necessary modular box duly concealed in wall including cost and conveyance of all material and all labour charges etc., complete for light and bell points in R.B. Copper cable Makes : Finolex / RR kabel / Havells / Polycab / KEI (HFFR) / V-Guard (HFFR) of Switch Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana | [6 empty] | Digital Key Telephone with 2 line display
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount | 50pair Telephone distribution box
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.7 | day | 1 | day | 735 |  | 20 pair Telephone distribution box with back mount frame
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1.4 | day | 1 | day | 615 |  | Caller ID Pushbutton
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.7 | day | 1 | day | 615 |  | 2Port Line Protection
|  |  | Labour Rate Per 7 pts | [6 empty] | 600 mm width x 500 mm net work rack
|  |  | Labour Rate for 1 pt | [6 empty] | Modular telephone Jack with connector
|  |  | Add GHMC allowance @40% | [6 empty] | LAN Cable cat - 6 UTP cable
|  |  | Labour Sub total | [6 empty] | 8 Port D-Link Desktop Switch
|  |  | b) Material | [6 empty] | 3 feet length moulded patch cord
| ELEC-1.5.1-a | 4 | Supply of (1.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as per IS:694/1990 specification for Copper cable of makes : Finolex / RR kabel / Havells / Polycab /Beljin (HFFR) /Ollvin(HFFR) / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million(HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (FRLS / HFFR) / Bonton (HFFR) and Avocab (HFFR) / Fortune Arrt (HFFR) / SPM (HFFR) / Sudhakar (HFFR) / Nakoda (HFFR) / HPL (HFFR) / GLOSTER (HFFR) / Rajnigandha (HFFR) / Pawancab (HFFR) / South King (HFFR). | 100 | Mtrs | 100 | Mtr | 2410 |  | Wireless-N300 Routewith RJ 45 Jacks
| ELEC-1.7.1.m | 5 | Supply of 3 Plate Jumbo Ceiling Rose of Makes : GM G Home / Gold Medal Olive / Million Zoom / Anchor Penta Cherry / Great white Omega / HPL / Vimal / CPL. | 7 | Nos | 1 | No | 25 |  | 600 mm width x 500 mm network Rack
| ELEC-1.3.1.b | 6 | Supply of 3 Module box. | 1 | Nos | 1 | No | 110 |  | RG-6 Cu flexible cable
| ELEC-1.3.1.c | 7 | Supply of 4 Module box. | 1 | Nos | 1 | No | 130 |  | Cat 6 RJ 45 Outlet
| ELEC-1.3.3.b | 8 | Supply of 3 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 105 |  | TV Socket
| ELEC-1.3.3.c | 9 | Supply of 4 Modular Cover Frame of makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 120 |  | 2.0/1.8 TR Split AC's
| ELEC-1.9.2.a | 10 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 7 | Nos | 1 | No | 85 |  | 1.5 TR Split AC's
|  |  | Total material cost for 7 pts | [6 empty] | Copper Pipe
|  |  | Total material cost for 1 pt | [6 empty] | 3core 2.5 Sqmm
|  |  | Total Material and Labour charges for 1 pt | [6 empty] | CPVC Pipe
|  |  | Add Overhead @ 10.615% | [6 empty] | Core Cutting
|  |  | Total Rate | [6 empty] | 1.00 HP Open Well Motor
|  |  | Rounded off rate | [6 empty] | Control Panel
|  |  | Fan and Exhaust Fan Points in RB | [6 empty] | 25mm GI Pipe
|  |  | Data-4 | [6 empty] | 25mm Gate Valve
4 | 24-25-RSD 2.1.2 |  | Wiring with 3 runs of (1.5 Sq.mm) FRLS / HFFR PVC insulated flexible ISI marked copper cable in existing consealed pipe including supply and fixing of 3 Plate Jumbo Ceiling rose of GM G Home / Gold Medal Olive / Million Zoom / Anchor Penta Cherry / Great white Omega / HPL / Vimal / CPL make , 10A ISI marked Modular type switch with cover frame and necessary modular box duly concealed in wall including cost and conveyance of all material and all labour charges etc., complete for fan and exhaust fan points in Residential Buildings of Copper cable Makes : Finolex / RR kabel / Havells / Polycab / KEI (HFFR) / V-Guard (HFFR) Switch Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana | [6 empty] | 3 Core 4.0 Sqmm Flat Copper Cable
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount | Water Dispenser
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.7 | day | 1 | day | 735 |  | Water Purifier
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1.4 | day | 1 | day | 615 |  | 40 KVA DG Set
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.7 | day | 1 | day | 615 |  | 125A 4 Pole Changeover
|  |  | Labour Rate Per 7 pts | [6 empty] | 125A 4 Pole MCCB
|  |  | Labour Rate for 1 pt | [6 empty] | Independent Copper earthing
|  |  | Add GHMC allowance @40% | [6 empty] | Independent GI earthing
|  |  | Labour Sub total | [6 empty] | GI Strip
|  |  | b) Material | [6 empty] | Copper Strip
| ELEC-1.5.1-a | 4 | Supply of (1.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as per IS:694/1990 specification for Copper cable of makes : Finolex / RR kabel / Havells / Polycab /Beljin (HFFR) /Ollvin(HFFR) / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million(HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (FRLS / HFFR) / Bonton (HFFR) and Avocab (HFFR) / Fortune Arrt (HFFR) / SPM (HFFR) / Sudhakar (HFFR) / Nakoda (HFFR) / HPL (HFFR) / GLOSTER (HFFR) / Rajnigandha (HFFR) / Pawancab (HFFR) / South King (HFFR). | 150 | Mtrs | 100 | Mtr | 2410 |  | 4 Passeneger Lift
| ELEC-1.7.1.m | 5 | Supply of 3 Plate Jumbo Ceiling Rose of Makes : GM G Home / Gold Medal Olive / Million Zoom / Anchor Penta Cherry / Great white Omega / HPL / Vimal / CPL. | 7 | Nos | 1 | No | 25 |  | 20Pair Telephone Distribution Box
| ELEC-1.3.1.b | 6 | Supply of 3 Module box. | 1 | Nos | 1 | No | 110 |  | Modular Telephone Jack
| ELEC-1.3.1.c | 7 | Supply of 4 Module box. | 1 | Nos | 1 | No | 130 |  | LAN Cable CAT-6 UTP
| ELEC-1.3.3.b | 8 | Supply of 3 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 105 |  | 8 Port D-Link DGS-1008A 8-Port Gigabit Switch
| ELEC-1.3.3.c | 9 | Supply of 4 Modular Cover Frame of makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 120 |  | D-Link DIR-615 Wireless-N300 Router
| ELEC-1.9.2.a | 10 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 7 | Nos | 1 | No | 85 |  | 6U Wall mounting Rack
|  |  | Total material cost for 7 pts | [6 empty] | Cat 6 RJ-45 information outlets
|  |  | Total material cost for 1 pt | [6 empty] | Modular co-Axial socket type TV Antenna outlet
|  |  | Total Material and Labour charges for 1 pt | [6 empty] | LED Bulbs
|  |  | Add Overhead @ 10.615% | [6 empty] | Batten Holders
|  |  | Total Rate | [6 empty] | 2Module boxes with cover frame
|  |  | Rounded off rate | [6 empty] | 3 Modular switch boards with cover frame
|  |  | Common Switch Board | [6 empty] | 4 Module boxes with cover frame
|  |  | Data-5 | [6 empty] | 6 Modular switch boards with cover frame
5 | 24-25 RSD 2.1.4 |  | Supply and fixing of ISI Marked 10A 3/2 pin Modular socket with shutter with 10A 1way Modular switch and cover frame on a common switch board with Module box with connections including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | [6 empty] | 8Module boxes with cover frame
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount | 12 Module switch boards with cover frame
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.067 | day | 1 | day | 735 |  | 18 Module boxes with cover frame
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.067 | day | 1 | day | 615 |  | 10A 3/2 Pin 2 Module Modular Socket with shutter.
|  |  | Labour for 1 Point | [6 empty] | 16A sockets
|  |  | Add GHMC allowance @40% | [6 empty] | 6/10 switches
|  |  | Labour Sub total | [6 empty] | 16/20 switches
|  |  | b) Material | [6 empty] | 63A FP Isolators
| ELEC-1.3.1.b | 3 | Supply of 3 Module box. | 1 | Nos | 1 | No | 110 |  | 6-32A MCBs
| ELEC-1.3.3.b | 4 | Supply of 3 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 105 |  | Water Geyser
| ELEC-1.9.2.a | 5 | Supply of 6/10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 85 |  | Run of 3 1.5 sq mm
| ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus/ Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 125 |  | 19/20 mm PVC bends
|  |  | Total material cost | [6 empty] | 20mm SWR Flexible Conduit Pipe
|  |  | Total Material and Labour charges for 1 no | [6 empty] | 6/10 2 Way switches
|  |  | Add Overhead @ 10.615% | [6 empty] | 10A Modular Bell Push with Neon Indicator
|  |  | Total Rate | [6 empty] | 20A 2 Module Modular Socket with shutter
|  |  | Rounded off rate | [6 empty] | 25 to 32A Modular type Motor Starter Switch
|  |  | Power Plug | [6 empty] | WPTC 6 sq mm
|  |  | Data-6 | [6 empty] | Casing And Capping 25 mm
6 | 24-25 RSD 2.1.6 |  | Supply and fixing of ISI marked 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter, 16 Amps Modular switch on a 3 Modular box with suitable cover frame with connections including cost and conveyance of all material and all labour charges etc., complete in N.R.B. / R.B. Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana | [6 empty] | 4P 63 A MCBs
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount | 6 way VTPN DB
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.1 | day | 1 | day | 735 |  | 8'' Exhaust Fan with Shutters
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 615 |  | 18 W LED Slimline Panel Light
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 615 |  | 1.5 HP Open well Submersible
|  |  | Labour for 1 No | [6 empty] | 3 Core x 2.5 Sqmm Flat Copper Cable for Motors
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.b | 4 | Supply of 3 Module box. | 1 | Nos | 1 | No | 110
| ELEC-1.3.3.b | 5 | Supply of 3 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 105
| ELEC-1.9.2.h | 6 | Supply of 16A / 20A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 110
| ELEC-1.9.2.L | 7 | Supply of 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 180
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Power Plug Two Nos
Data-7
7 | 24-25 RSD 2.1.6X2 |  | Supply and fixing of 2 No.s ISI marked 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter, 16 Amps Modular switch on suitable Modular box with suitable cover frame with connections including cost and conveyance of all material and all labour charges etc., complete in N.R.B. / R.B. Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.2 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.2 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.2 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.d | 4 | Supply of 6 Module box. | 1 | Nos | 1 | No | 164
| ELEC-1.3.3.d | 5 | Supply of 6 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 138
| ELEC-1.9.2.h | 6 | Supply of 16A / 20A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 2 | Nos | 1 | No | 106
| ELEC-1.9.2.L | 7 | 16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 2 | Nos | 1 | No | 173
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
6Module (6A Sockets & -6A Switches - Two Nos)
Data-8
8 | 24-25 RSD 2.1.4X2 |  | Supply and fixing of 2 no.s ISI Marked 10A 3/2 pin Modular socket with shutter with 2 No.s 10A 1way Modular switch and cover frame on a common switch board with Module box with connections including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. |  | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. |  | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.d | 3 | Supply of 6 Module box. | 1 | Nos | 1 | No | 180
| ELEC-1.3.3.d | 4 | Supply of 6 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 180
| ELEC-1.9.2.a | 5 | Supply of 10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 2 | Nos | 1 | No | 85
| ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 2 | Nos | 1 | No | 125
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
12Module (6A Sockets & -6A Switches - Four Nos)
Data-9
9 | 24-25 RSD 2.1.4X4 |  | Supply and fixing of ISI marked 4 Nos 10A Modular type switches with 4 Nos 10A 3/2 pin Modular plug sockets with shutter on 12 Modular box with cover frame including connections, cost and coveyance of all material and all labour charges etc., complete for Computers in N.R.B. / R.B. Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.25 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.25 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.f | 3 | Supply of 12 Module box. | 1 | Nos | 1 | No | 285
| ELEC-1.3.3.f | 4 | Supply of 12 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana | 1 | Nos | 1 | No | 285
| ELEC-1.9.2.a | 5 | Supply of 10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 4 | Nos | 1 | No | 85
| ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 4 | Nos | 1 | No | 125
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
8 Module switch Board (6A Sockets & 6A Switches-3 Nos)
Data-10
10 | 24-25 RSD 2.1.4X3 |  | Supply and fixing of ISI marked 3 Nos 10A Modular type switches with 3 Nos 10A 3/2 pin Modular plug sockets with shutter on 9 Modular box with cover frame including connections, cost and coveyance of all material and all labour charges etc., complete for Computers in N.R.B. / R.B. Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.2 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.2 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.e | 3 | Supply of 8/9 Horizontal/Vertical Module box. | 1 | Nos | 1 | No | 235
| ELEC-1.3.3.e | 4 | Supply of 8 Modular Cover Frame of Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana. | 1 | Nos | 1 | No | 230
| ELEC-1.9.2.a | 5 | Supply of 10A 1 Way 1 Module Modular Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 3 | Nos | 1 | No | 85
| ELEC-1.9.2.d | 6 | Supply of 10A 3/2 Pin 2 Module Modular Socket with shutter of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 3 | Nos | 1 | No | 125
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
1200mm length LED light
Data-11
11 | SD-N.A |  | Supply, Transportation and fixing of 22W, 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 50,000 burning hours with BIS Certification with BIS Certification. .duly erected duly erected on 2 Nos suitable clip type holders with all connections with twin core copper wire of Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Q-FLX / Gemini / Vimal / Suncab / Pawancab and labour charges etc complete. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / IB LED / Panasonic / Halonix / HPL / Syska / Eveready / Surya / Keselec. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. ,
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.1 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC-1.5.4 | 3 | Supply of 23 / 0060 3 core (0.15 mm dia of each lead) twisted / flat heavy Copper wire. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Q-FLX / Gemini / Vimal / Suncab / Pawancab. | 0.5 | Mtr | 100 | Mtrs | 1325
|  | 4 | suitable clip type holders | 2 | Nos | 1 | Nos | 10
| ELEC 1.4.4-d | 5 | Supply of No.8 Screws of 35/38mm. | 2 | Nos | 100 | Nos | 135
| ELEC-10.1.2 | 6 | Rawl Plugs. | 2 | Nos | 100 | Nos | 45
Cost of Material for fixing luminaire
| ELEC-3.3.16 | 7 | Supply and transportation of 22W, 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 5 years warranty with BIS Certification with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / IB LED / Panasonic / Halonix / HPL / Syska / Eveready / Surya / Keselec. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. | 1 | No | 1 | No | 615
Cost of Material
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
15W LED Slimline Panel Light
Data-12
12 | SD-NA |  | Supply and transportation and fixing of 15W (1350Lm) edge lit LED slimline panel light Housing made of Pressure die cast aluminium with Powder coated, round / Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE : Phillips /Wipro / Crompton / Bajaj / Havells / Jaquar / IB LED / Panasonic / Halonix / HPL / Syska / Eveready / Surya / Keselec/ FIEM / Arraystorm / GM / Goldmedal . LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.062 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.062 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.062 | day | 1 | No | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC- 3.3.7-c | 4 | Supply and transportation of 15W (1350Lm) edge lit LED slimline panel light Housing made of Pressure die cast aluminium with Powder coated, round / Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE : Phillips /Wipro / Crompton / Bajaj / Havells / Jaquar / IB LED / Panasonic / Halonix / HPL / Syska / Eveready / Surya / Keselec/ FIEM / Arraystorm / GM / Goldmedal . LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. | 1 | no | 1 | no | 920
|  | 5 | Alluminium Flat,screws / hooks,binding wire (As per requirement). | [5 empty] | 20
Cost of Material for fixing luminaire
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
36W 2' x2' (600mm x 600mm) slim panel LED
Data-13
13 | SD-NA |  | Supply and Transportation and fixing of 36W.Edge lit, 2' x2' (600mm x 600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% with non integrated driver etc., complete with 50,000 burning hours with BIS Certification. LUMINAIRE MAKE : Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / IB LED / Panasonic / Halonix / HPL / Syska / Eveready / Surya / Keselec. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.125 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.125 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.125 | day | 1 | No | 615
Labour for 1 No
Add Muncipality area allowance (Mahbubnagar)@20%
Labour Sub total
b) Material
| Elec 3.3.17 a | 4 | Supply and Transportation of .36W Edge lit, 2' x2' (600mm x 600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% with non integrated driver etc., complete with 50,000 burning hours with BIS Certification. LUMINAIRE MAKE : Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / IB LED / Panasonic / Halonix / HPL / Syska / Eveready / Surya / Keselec. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. | 1 | no | 1 | no | 2780
|  | 5 | Alluminium Flat,screws / hooks,binding wire (As per requirement) | [5 empty] | 48
Cost of Material for fixing luminaire
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Ceiling Fans
Data-14
14 | 24-25 RSD 9.7.2+ RSD9.7.35 |  | Supply, Transportation and fixing of energy efficient fan,1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current(BLDC)motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 7.85, Air delivery minimum 270 CMM, 275 RPM(tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete including all standard accessories and labour charges for fixing of ceiling fan with connections with twin core copper wire of Finolex / RR Kabel / Havells / Polycab and labour charges etc complete. Makes : Atomberg (Efficio ) / Havells /Orient
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.125 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.125 | day | 1 | day | 615
|  |  | Deduct labour for not fixing Regulator | -0.1 | Nos | 1 | Nos | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| Elec- 1.5.4 | 3 | Supply of 23 / 0060 , 3 core (0.15 mm dia of each lead) twisted / flat heavy Copper wire of Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Q-FLX / Gemini / Vimal / Suncab / Pawancab | 1 | Mtr | 100 | Mtrs | 1325
| Elec-5.1.3 | 4 | Supply, Transportation of energy efficient decorative fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current(BLDC)motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMM/W) greater than 8.5, Air delivery minimum 235 CMM, 350 RPM (tolerance as per IS:374-2019), THD less than 10%, remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C (max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing.etc., complete of Makes : Atomberg (Efficio + ) / Havells / Orient / RR / Halonix. | 1 | Nos | 1 | Nos | 3275
|  |  | Transportation of material |  |  |  |  | 1%
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Stepped Electronic Regulator
Data-15
15 | 24-25 RSD 9.7.26 |  | Supply and fixing of 2 Module Modular type Stepped electronic regulator with connections and Labour charges etc complete. Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | Nos | 1 | Nos | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.n | 2 | Supply of 2 Module Modular type Electronic Fan Regulator of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | Nos | 500
Total material cost
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Exhaust Fan
Data 16
16 | 24-25 RSD 9.7.2+RSD 9.7.36 |  | Supply, Transportation and Fixing of 12" (300mm)Light duty exhaust fan with metal blades etc completewith all labour charges etc., complete as directed at site . Makes : Crompton / Havells Ventilair-DB / Orient hill air.
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.25 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.25 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
|  | 3 | Sundries such as Bolt, Nuts, twin core wire if necessary etc. |  |  |  |  | 15
Cost of Material for fixing fan
b) Material
| ELEC-5.1.14 b | 4 | Supply of 12" (300mm)Light duty exhaust fan with metal blades etc complete of Makes : Crompton / Havells Ventilair-DB / Orient hill air. | 1 | No | 1 | No | 1730
|  |  | Transportation Charges on Unit Cost @1% |  |  |  |  | 1%
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Ding Dong Bell
Data-17
17 | 24-25 RSD-2.1.13 |  | Supply and fixing of Ding Dong Bell of makes GM / Million / Gold Medal / Anchor / Great white,in lieu of Ceiling rose, including giving connections, cost of all accessories and labour charges etc., complete.
Makes : GM / Million / Gold Medal /Anchor / Great White.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.062 | No | 1 | No | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.062 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-1.7.2 b | 3 | Supply of Ding Dong Bell of Makes : GM / Million / Gold Medal / Anchor / Great white. | 1 | Nos | 1 | No | 125
Cost of Material
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Musical Bell
Data-18
18 | 24-25 RSD-2.1.13 |  | Supply and fixing of Electronic Musical Bell of Makes : GM / Million / Gold Medal / Anchor / Great white in lieu of Ceiling rose including giving connections, cost of all accessories and labour charges etc., complete .
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.062 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.062 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC-1.7.2 c | 3 | Supply of Electronic Musical Bell of Makes : GM / Million / Gold Medal / Anchor / Great white. | 1 | Nos | 1 | No | 280
Total material cost
Total Material and Labour charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Run of 3 of 2.5 Sq.mm Copper Cable
Data 19
19 | 24-25 RSD 3.1.4 |  | Supply and Run of 3 of (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing pipe for run of mains inlcuding all labour charges etc., complete
Copper Cable Makes : Finolex / RR kabel / Polycab / Havells / KEI (HFFR) / L&T / V-Guard (HFFR).
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.67 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.67 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-1.5.1-b | 4 | Supply of (2.5 Sqmm) FRLS / HFFR PVCinsulated 1100V grade as per IS:694/1990 specification for of Copper Cable Makes : Finolex / RR kabel / Havells / Polycab /Beljin (HFFR) /Ollvin(HFFR) / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million(HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (FRLS / HFFR) / Bonton (HFFR) and Avocab (HFFR) / Fortune Arrt (HFFR) / SPM (HFFR) / Sudhakar (HFFR) / Nakoda (HFFR) / HPL (HFFR) / GLOSTER (HFFR) / Rajnigandha (HFFR) / Pawancab (HFFR) / South King (HFFR). | 300 | Mtrs | 100 | Mtrs | 3900
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Run of 3 of 4.0 Sq.mm Copper Cable
Data 20
20 | 24-25- RSD 3.1.5 |  | Supply and Run of 3 of (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing pipe for run of mains inlcuding all labour charges etc., complete
Copper Cable Makes : Finolex / RR kabel / Havells / APAR EBXL / KEI (HFFR) / Polycab ((HR_FR-LF) / L&T / V-Guard (HFFR).
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 3 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-1.5.1-c | 4 | Supply of (4.00 Sq.mm) FRLS / HFFR PVC insulated 1100V grade as per IS:694/1990 specification for Copper Cable Makes : Finolex / RR kabel / Havells / Polycab /Beljin (HFFR) /Ollvin(HFFR) / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million(HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (FRLS / HFFR) / Bonton (HFFR) and Avocab (HFFR) / Fortune Arrt (HFFR) / SPM (HFFR) / Sudhakar (HFFR) / Nakoda (HFFR) / HPL (HFFR) / GLOSTER (HFFR) / Rajnigandha (HFFR) / Pawancab (HFFR) / South King (HFFR). | 300 | Mtrs | 100 | Mtrs | 5950
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Run of 5 of 6.0 Sq.mm Copper Cable
Data 21
21 | 24-25 RSD 3.1.6X2 |  | Supply and Run of 5 of (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing pipe for run of mains inlcuding all labour charges etc., complete
Copper Cable Makes : Finolex / RR kabel / Havells / APAR EBXL / KEI (HFFR) / Polycab ((HR_FR-LF) / L&T / V-Guard (HFFR).
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 6 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-1.5.1-d | 4 | Supply of (6.0 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for "Copper Cable Makes : Finolex / RR kabel / Havells / APAR EBXL / KEI (HFFR) / Polycab ((HR_FR-LF) / L&T / V-Guard (HFFR).ELEC-1.5.1-d) | 500 | Mtrs | 100 | Mtrs | 8790
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
4Way TPN DB
Data 22
22 | 24-25 RSD 4.4.4A |  | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for and for 1 No 4 pole Incommer with 1 No 63A FP Isolator and 12 Nos 6-32 A 10kA SP MCBs as out goings of including internal connections and labour charges for Flush Mounting etc., complete
DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | a) Labour charges for Flush Mounting | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 4 | Semi Skilled Mason. SOR-2024-25 Sl No 35 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-10.4.10 | 5 | Cement. | 12.5 | Kg | 1 | Kg | 9
| ELEC-2.16.1-b | 6 | Supply of (8+12) 4 Way TPN DB Horizontal with IP 43, 12 Nos Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos S.P. out goings and for 1 No 4 pole Incommer etc complete ofMakes : Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S. | 1 | Nos | 1 | No | 4600
| ELEC-2.14.1-g | 7 | Supply of 63A FP Isolator of Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree / Indo Asian / BCH . | 1 | Nos | 1 | No | 1440
| ELEC-2.13.1 -a | 8 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree / Indo Asian / BCH. | 12 | Nos | 1 | No | 325
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
8Way VTPN DB
Data-23
23 | 24-25 RSD 4.4.8 |  | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No 125A , 4 Pole MCCB, 25KA with 6 Nos 50-63A TP MCB 10KA, 6 Nos 6-32A SP, 10KA , C/D Curve ISI Marked MCBs including connections, terminations glands, lugs and labour charges for Flush Mounting etc., complete D BMakes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree Xpro. MCCB Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | MATERIAL | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Supply of 8 Way VTPN DB with IP 43 Protection as per IS:13032 and suitable for accommodating T.P. / S.P. as out goings and 125A / 160A 4 pole MCCB as Incommer etc complete (SOR--2.16.2a)
|  |  | Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. | 1 | No | 1 | No | 16458
| ELEC-2.13.1 -a | 2 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3 / Schneider-Acti9 /Siemens / LK (L&T) Exora / Crabtree / Indo Asian / BCH | 6 | No | 1 | No | 325
| ELEC-2.13.1 -i | 3 | Supply of 50-63A 10KA TP MCB, C/D Curve ISI Mark of make Legrand-DX3 / Schneider-Acti9 /Siemens / LK (L&T) Exora / Crabtree / Indo Asian / BCH | 6 | No | 1 | No | 2375
| ELEC-2.7.1 -d | 4 | Supply of 125A , 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25KA with thermal magnetic release Panel Mounted of Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH. | 1 | No | 1 | No | 13770
| ELEC-10.4.10 | 5 | Cement. | 12.5 | Kg | 1 | Kg | 9
Cost of Material for 1 No
LABOUR
|  | 6 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 695
|  | 7 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 580
|  | 8 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 580
|  | 9 | Semi Skilled Mason. SOR-2024-25 Sl No 35 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 580
COST OF LABOUR
Add GHMC Allowance @40%
Labour Sub total
cost of material +Labour
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Water Heater (Geysers)
Data 24
24 | Finished item |  | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type Vertical / Horizontal 230/250V single phase 2000watts ISI mark 5 Star rated water heater with ABS plastic body of 25 ltrs capacity to withstand up to 8.0 bar of water pressure including all standard accessories and dead weight pressure reducing valve on out let side, including cost of 2 Nos SS flexible braided hose pipe, testing and all labour charges etc., complete. Makes : Crompton / Jaquar / Venus / Racold / AO Smith / Havells / Bajaj or equivalent as approved by the Dept.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-5.2.1 b | 1 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type Vertical / Horizontal 230/250V single phase 2000watts ISI mark 5 Star rated water heater with ABS plastic body of 25 ltrs capacity to withstand up to 8.0 bar of water pressure including all standard accessories and dead weight pressure reducing valve on out let side, including cost of 2 Nos SS flexible braided hose pipe, testing and all labour charges etc., complete of Makes : Crompton / Jaquar / Venus / Racold / AO Smith / Havells / Bajaj or equivalent as approved by the Dept. | 1 | No | 1 | No | 12735
Cost of Material
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Water Heater hose pipe
Data 25
25 | Finished item |  | Supply, , Installation, Testing and Commissioning of Metallic / SS Flexible braided hose pipe
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-5.3.4 | 1 | Supply, , Installation, Testing and Commissioning of Metallic / SS Flexible braided hose pipe. | 1 | No | 1 | No | 220
Cost of Material
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Street Light
Data-26
26 | SD-NA |  | Supply transportation and fixing of 120W LED Street light Body made of high grade pressure die – cast Aluminium alloy with corrosion resistant powder coat, having protective toughened glass cover, Less Glare, IP 66 (Silicon gasket ensures Optical & Electrical compartments are IP 66) protected, wide operating voltage range, P.F > 0.90, System having efficacy >100 lumens/watt, with Ingress protection IP66, Potted driver, Driver surge protection >10KV, THD<15%, CCT: 3000- 6500K as desired by the department and as per IS, CRI>80, Inbuilt Electrical protections like Over voltage, short circuit, Over load, Open Circuit, Miswiring, etc complete with BIS certification with warranty 50,000 burning hours. The contractor has to furnish the manufacturer warranty letter, LM 79 and LM 80 certificates. LUMINAIRE MAKE : PHILIPS / OSRAM / GE Venture / CROMPTON / BAJAJ / Wipro / Jaquar / Eveready / Halonix / Keselec / HAVELLS / POLYCAB / SURYA / SYSKA. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. as desired by the department and fixing the luminaire with 1.0 Mtr 40mm dia 'B' Class GI pipe bracket, 2 nos anti tilting MS flats and connections with 2 of WPSC / 1 of WPTC of 2.5 Sqmm wire ISI marked.of Makes : Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Gemini / Vimal / Suncab / Stanjo / Rajnigandha / Orbit / Airson. ,etc complete.
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.125 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.125 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.125 | day | 1 | No | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| Elec-1.6.1 | 4 | Supply of 2.5 Sqmm WPSC (Weather Proof Single Core) (ELEC-1.6.1 a) ISI Alluminium Wire of Makes : Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Gemini / Vimal / Suncab / Stanjo / Rajnigandha / Orbit / Airson. | 1.5 | Mtrs | 100 | Mtrs | 960
| TBSP-G.I-11 | 5 | 40mm Nominal Bore Medium grade G.I.Pipe | 1 | Mtrs | 1 | Mtrs | 510
|  | 6 | Pipe bending charges |  |  |  |  | LS | 20
|  | 7 | 2 nos M.S flat and welding charges, screws etc |  |  |  |  | LS | 50
Cost of Material for fixing luminaire
| ELEC-3.5.1-I | 8 | Supply and transportation of 120WLED LED Street light Body made of high grade pressure die – cast Aluminium alloy with corrosion resistant powder coat, having protective toughened glass cover, Suitable lens on LEDs, Less Glare, IP 66 (Silicon gasket ensures Optical & Electrical compartments are IP 66) protected, wide operating voltage range, P.F > 0.90, System having efficacy >110 lumens/watt, with Ingress protection IP66, Potted driver, Driver surge protection >10KV, THD<15%, CCT: 3000- 6500K as desired by the department and as per IS, CRI>70, Inbuilt Electrical protections like Over voltage, short circuit, Over load, Open Circuit, Miswiring, etc complete with BIS certification with 5 years warranty. The contractor has to furnish the manufacturer warranty letter, LM 79 and LM 80 certificates. LUMINAIRE MAKE : PHILIPS / OSRAM / GE Venture / CROMPTON / BAJAJ / Surya / Wipro / Jaquar / Eveready / Halonix /Keselec / HAVELLS / POLYCAB / SURYA / SYSKA / Capart / Fortune Arrt / FIEM / Panasonic / Arraystorm / GM / Goldmedal / Silicon / Leksa / Orient / HPL /Valmont Transrail, LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. | 1 | Nos | 1 | Nos | 8440
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Bollard
Data 27
27 | Finished item |  | Supply and Fixing of Circo Bollard including cost and coveyance of all material and all labour charges etc., complete of make K-Lite or its equivalent.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| Non SOR K-lite Pricelist | 1 | Supply and Fixing of Circo Bollard including cost and coveyance of all material and all labour charges etc., complete of make K-Lite or its equivalent. ( Approved rate MRC Qtrs) | 1 | No | 1 | No | 2710
Cost of Material
| Provisional rate | 2 | Labour for fixing | 1 | Job | 1 | Job | 320
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
3 Core x 2.5 Sqmm Armoured Cable
Data 28
28 | Finished item |  | Supply and laying of 2.5 Sqmm 3 Core PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete of Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI / Gloster / V-Guard / Finecab.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-1.5.7-h | 1 | Supply of 3core 2.5 Sqmm PVC / XLPE Insulated, Flexible Armouring Flexible Copper cable as per IS 7098 / Part-I / 1988 including all transportation charges etc complete of Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI / Gloster / V-Guard / Finecab / SPM/ Gemini / Unistar / Windsor / Payal / Fortune Arrt / Avocab / Nakoda / HPL / Sudhakar / Bonton / Rajnigandha / Pawancab / South King. | 1 | Mtrs | 1 | Mtrs | 155
Cost of Material
| Provisional rate | 2 | Labour for laying | 1 | Mtrs | 1 | Mtrs | 6
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Panel Board
Data-29
29 | SD-NA |  | Supply, installation, testing and commissioning of Wall mounting OUT DOOR type panel board with Aluminium bus bars fabricated with 14/16 Gauge (14 for Outer and 16 for Inner) CRCA Sheet comprising of bus bars with equal size in all phases and neutral equipped with bus bar chambers and cable chambers. The bus bars fault level shall be 50 KA and shall be as per the requirement of local CEIG, fire regulations, CPRI norms and other authorities etc. The painting of the complete system shall be powder coated duly processing the panel in 7 tank process . The panel shall be suitable for accomdating the following switch gear including supply of all components, hard wares etc including all necessary civil works, supporting anchor fasteners, bolts, suitable G.I earth strip 25 x 6 mm, door loop earthings , bus bars should be colour sleeved with heat shrinkable sleeves for phase and neutral duly supported at regular intervels by SMC supports and all cables shall have proper cable entry and shall be installed and consisting of the following as required and as per IS standards for OUT DOOR type.(Panel shall be manufacture only from CPRI approval fabricators.) INCOMINGS:- Supply of 250A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted of makes L&T / Schneider / Siemens / Legrand -1Nos OUTGOING:- 1) Supply of 125A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. of makes L&T / Schneider / Siemens / Legrand. - 4Nos EB Metering Equipment:- 1) Supply of Spreaders Links 125A 3 Pole MCCB of make Legrand - 8sets, 2) Supply of Spreaders Links 250A 4 Pole MCCB of make Legrand - 2sets, 3) Supply and erection of RYB LED indicator lamps on the existing box / panel board - 3Nos,
|  |  |  | Quantity |  | Unit |  | Rate | Amount
INCOMINGS:-
| ELEC-2.7.1-h | 1 | Supply of 250A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted of Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH. | 1 | Nos | 1 | No | 32940
OUTGOING:-
| ELEC-2.7.1-c | 2 | Supply of 125A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. of Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 11380
EB Metering Equipment:-
| ELEC-2.10.3-a | 3 | Supply and transportation of Spreaders Links 125A 3 Pole MCCB. | 8 | Nos | 1 | No | 270
| ELEC-2.10.3-f | 4 | Supply and transportation Spreaders Links 250A 4 Pole MCCB. | 2 | Nos | 1 | No | 1020
| ELEC-8.14.6-b | 5 | Supply and erection of RYB LED indicator lamps on the existing box / panel board of Makes : L&T / C&S / SALZAR / HPL. | 3 | Nos | 1 | No | 165
SUB-TOTAL 1
Sheet calculations
LXHXW = 1.3X1.2X0.35
| ELEC-8.13.1-a | 6 | Fabrication and erection of 14SWG CRCA(2mm) sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges.
|  |  | Top & Bottom Portions = 0.35 x 1.3 x 2Nos |  | sqmt
|  |  | Sides & Verticals = 0.35 x 1.2 x 2 Nos |  | sqmt
|  |  | F & B Portions = 1.2 x 1.3 x 2Nos |  | sqmt
|  |  | Sub total |  | sqmt
|  |  | Wastage @ 10% |  | sqmt
|  |  | Grand Total (SOR 24-25 ELEC-7.13.1 A ) |  | sqmt | 1 | sqmt | 6185
| ELEC-8.13.1-b | 7 | Fabrication and erection of 16SWG CRCA(1.6mm) sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges.
|  |  | Front side Portions = 1.2 x 1.3 x 1 Nos |  | sqmt
|  |  | Sides & Verticals = 0.35 x 1.2 x 3 Nos |  | sqmt
|  |  | Horizontals Portions = 0.35 x 0.35 x 3Nos |  | sqmt
|  |  | Sub total |  | sqmt
|  |  | Wastage @ 10% |  | sqmt
|  |  | Grand Total (SOR 24-25 ELEC-7.13.1 B ) |  | sqmt | 1 | sqmt | 5770
| ELEC-9.3.4 | 8 | Bus Bar details (SOR 2024-25 ELEC-9.3.4)
|  |  | For phases & neutral (30x10x1.2*2.7)/1000*4 | 3.88 | Kg | 1 | Kg | 406
|  |  | For Earth (25x6x1.3*2.7)/1000*1 | 0.526 | Kg | 1 | Kg | 406
|  |  | Links (25*6*0.5m*4*2.7/1000=0.810kg) | 0.81 | Kg | 1 | Kg | 406
Sub-Total 2
Sub-Total (1+2)
|  | 9 | Control wiring, labour charges for erection of switchgear,angle iron for wall mounting, panel board including all labour charges etc. with connections for finished items of works including transportation charges etc. @ 5%
L.S. Towards unforeseen items and rounding off.
|  |  | Grand Total | [5 empty] | 137000
Add Overhead @ 10.615%
Total Rate
Rounded off rate
4way SPN DB
Data-30
30 | 24-25 RSD 4.4.2b |  | Supply and fixing of 4 Way SPN DB with IP 43 Protection as per IS:13032 including Supply and Fixing of 1 No 63A FP Isolator with all connections and labour charges etc., complete for Flush Mounting . DBMakes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree Xpro. Isolator Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | LABOUR | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 4 | Semi Skilled Mason. SOR-2024-25 Sl No 35 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 615
COST OF LABOUR for 1 no
Add GHMC Allowance @40%
Labour Sub total
MATERIAL
| ELEC-10.4.10 | 5 | Cement. | 4 | Kg | 1 | Kg | 9
| ELEC-2.15.1-b | 6 | Supply of 4 Way SPN DB with IP 43 Protection as per IS:13032 and suitable for 4 Nos S.P out goings and for 1 No Incomer with 100 A tinned copper busbar, neutral bar, earth bar and cable ties for cable management, fully shrouded neutral bar, din bars and detachable gland plate etc complete with inter connections. Makes : Legrand / Schneider / Siemens / LK / Crabtree Xpro / ABB / C&S / BCH. | 1 | Nos | 1 | No | 1750
| ELEC-2.14.1-g | 7 | Supply of 63A FP Isolator of Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 1 | Nos | 1 | No | 1440
Cost of Material
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
8way SPN DB
Data-31
31 | 24-25 RSD 4.4.2b |  | Supply and fixing of 8 Way SPN DB with IP 43 Protection as per IS:13032 including Supply and Fixing of 1 No 40A DP Isolator and 6 Nos 6-32A 10kA ISI Marked C/D curve SP MCBs with all connections and labour charges etc., complete for flushMounting . DBMakes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree Xpro. Isolator Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | LABOUR | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 4 | Semi Skilled Mason. SOR-2024-25 Sl No 35 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 615
COST OF LABOUR for 1 no
Add GHMC Allowance @40%
Labour Sub total
MATERIAL
| ELEC-10.4.10 | 5 | Cement. | 4 | Kg | 1 | Kg | 9
| ELEC-2.15.1-d | 6 | Supply of 8 Way SPN DB with IP 43 Protection as per IS:13032 and suitable for 8Nos S.P out goings and for 1 No Incommer etc complete DB of Makes : Legrand / Schneider / Siemens / LK / Crabtree Xpro / ABB / C&S / BCH | 1 | Nos | 1 | No | 2200
| ELEC-2.14.1-b | 7 | Supply of 40A DP Isolator of DB Makes : Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / LK (L&T) Exora / Cabtree / Indo Asian / BCH | 1 | Nos | 1 | No | 590
| ELEC-2.13.1 -a | 8 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree / Indo Asian / BCH. | 6 | No | 1 | No | 325
Cost of Material
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Run of 1 of 1.50 Sq.mm
Data 32
32 | 24-25 RSD 3.1.2 |  | Supply and Run of 1 of (1.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing pipe for UPS points inlcuding all labour charges etc., complete.
Copper Cable Makes : Finolex / RR kabel / Havells / APAR EBXL / KEI (HFFR) / Polycab ((HR_FR-LF) / L&T / V-Guard (HFFR).
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-1.5.1-a | 4 | Supply of (1.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as per IS:694/1990 specification for Copper cable of makes : Finolex / RR kabel / Havells /Polycab / Beljin (HFFR) / Finecab Gold (HFFR) / GM (HFFR) / Gold Medal (HFFR) / Million(HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (FRLSH/ HFFR) / Bonton (HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Sudhakar (HFFR) / Nakoda (HFFR) / HPL (HFFR) / GLOSTER(HFFR) / Rajnigandha (HFFR) / Pawancab (HFFR) / South King (HFFR) | 100 | Mtrs | 100 | Mtr | 2410
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Rounded of Rate
70 Sqmm Cable
Data 33
33 | Finished item |  | Supply of70 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Payal / RR kable / Beljin / Ollvin / Finecab / RPG / V - Guard / Orbit / Fortune Arrt /Gemscab / Bonton / SPM / Unistar / Windsor/ Avocab / Pawancab / Nakoda / Suncab
b) Material
| SOR 24-25 ELEC-4.1.1J |  | Supply of 70 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Payal / RR kable / Beljin / Ollvin / Finecab / RPG / V - Guard / Orbit / Fortune Arrt /Gemscab / Bonton / SPM / Unistar / Windsor/ Avocab / Pawancab / Nakoda / Suncab | 1 | Mtrs | 1 | Mtr | 730
Cost of Material
Laying of 70 Sqmm Cable
Data-34
34 | 24-25 RSD 15.6.3 |  | Laying of PVC armoured under ground cable 3.5 Core 70 Sqmm fixing on chromium plated metallic base saddles on wall as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete.
|  |  | b) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 4 | day | 1 | day | 615
Labour Charges for 100 Mtrs
Labour Charges for 1 Mtr
Add GHMC Allowance @40%
Labour Sub total
a) Material
| Elec-1.4.4 e | 3 | Supply of No.8 Screws of 50mm.(SOR-2024-25-Elec-1.4.4 e) | 400 | Nos | 100 | Nos | 155
|  | 4 | Supply of Saddle / Clamps suitable for fixing 3.5 Core 70 Sqmm Cable (SOR-2024-25 ELEC-10.4.22 f) | 200 | Nos | 100 | Nos | 735
|  |  | Cost of Material for laying of cable for 100mtr | 100 | Mtrs
|  |  | Cost of Material for laying of cable for 1 mtr | 1 | Mtrs
Total Cost of Material + Labour Charges
Rounded off rate
Earthwork excavation of UG Cable
Data-35
35 | 24-25 RSD 15.6.1 |  | Earth work excavation of Trench in hard ground soil upto a depth of 0.9 mts and laying of U.G cables up to 50 sqmm covering the cable with bricks and back filling of Trench including cost and conveyance of materials and labour charges etc., complete..
|  |  | b) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
|  | 3 | Man Mazdoor -UN-SKILLED CATEGORYSOR-2024-25 III :item Nos 3/4 | 2.5 | day | 1 | day | 615
Labour Charges for 100 Mtrs
Labour Charges for 1 Mtr
Add GHMC Allowance @40%
Labour Sub total
a) Material
| ELEC-10.4.15 | 4 | Earth Work Excavation (ELEC-10.4.15) | 27 | Cum | 1 | Cum | 318
100 x 0.3 x 0.90 Cu. Mtrs
| ELEC-10.4.12 | 5 | Bricks ELEC-10.4.12 | 920 | Nos | 1000 | Nos | 9702
|  |  | Cost of Material for laying of cable in trench for 1mtr | 100 | Mtrs
|  |  | Cost of Material for laying of cable in trench for 1 mtr | 1 | Mtrs
Total Cost of Material + Labour Charges
Rounded off rate
50 mm Nominal Bore GI pipe
Data 36
36 | Finished item |  | Supply and fixing of 50 mm Nominal Bore GI pipe Light Grade properties & weight as per IS 1239 ISI mark with GI fittings including the cost of pipe & its fittings & labour charges complete.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| SOR 24-25 TBSP-G.I-06 | 1 | Supply and fixing of 50 mm Nominal Bore GI pipe Light Grade properties & weight as per IS 1239 ISI mark with GI fittings including the cost of pipe & its fittings & labour charges complete. | 1 | Mtrs | 1 | Mtr | 519
Cost of Material
35 Sqmm Cable
Data 37
37 | Finished item |  | Supply of 35 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Payal / RR kable / Beljin / Ollvin / Finecab / RPG / V - Guard / Orbit / Fortune Arrt /Gemscab / Bonton / SPM / Unistar / Windsor/ Avocab / Pawancab / Nakoda / Suncab
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-4.1.1h | 1 | Supply of 35 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Payal / RR kable / Beljin / Ollvin / Finecab / RPG / V - Guard / Orbit / Fortune Arrt /Gemscab / Bonton / SPM / Unistar / Windsor/ Avocab / Pawancab / Nakoda / Suncab | 1 | Mtrs | 1 | Mtr | 430
Cost of Material
25 Sqmm Cable
Data 38
38 | Finished item |  | Supply of 25 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Makes :Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Payal / RR kable / Beljin / Ollvin / Finecab / RPG / V - Guard / Orbit / Fortune Arrt /Gemscab / Bonton / SPM / Unistar / Windsor/ Avocab / Pawancab / Nakoda / Suncab
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-4.1.1g | 1 | Supply of 25 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) of Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Payal / RR kable / Beljin / Ollvin / Finecab / RPG / V - Guard / Orbit / Fortune Arrt /Gemscab / Bonton / SPM / Unistar / Windsor/ Avocab / Pawancab / Nakoda / Suncab | 1 | Mtrs | 1 | Mtr | 360
Cost of Material
Laying of 35 & 25 Sqmm Cable
Data-39
39 | 24-25 RSD 15.6.3 |  | Laying of PVC armoured under ground cable 3.5 Core 25&35 Sqmm fixing on chromium plated metallic base saddles on wall as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete.
|  |  | b) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 4 | day | 1 | day | 615
Labour Charges for 100 Mtrs
Labour Charges for 1 Mtr
Add GHMC Allowance @40%
Labour Sub total
a) Material
| Elec-1.4.4 d | 3 | Supply of No.8 Screws of 35mm. | 400 | Nos | 100 | Nos | 135
| Elec-10.4.23 d | 4 | Supply of Saddle / Clamps suitable for fixing 3.5 Core 25&35 Sqmm Cable. | 200 | Nos | 100 | Nos | 468
|  |  | Cost of Material for laying of cable for 100mtr | 100 | Mtrs
|  |  | Cost of Material for laying of cable for 1 mtr | 1 | Mtrs
Total Cost of Material + Labour Charges
Rounded off rate
Speaker Cable
Data 40
40 | 24-25 RSD 3.1.2 |  | Supply, Installation, Testing and Commissioning of 1.5 Sq mm speaker cable etc., complete with connections
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC 14.1.11 | 4 | Supply, Installation, Testing and Commissioning of 1.5 Sq mm speaker cable etc., complete with connections | 100 | Mtrs | 1 | Mtrs | 76
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Rounded of Rate
4Module 3W LED Foot lamp
Data41
41 | 24-25 RSD 8.1.1 |  | Supply ,Transportation and fixing of 4Module 3W LED Foot lamp as desired by the department and as per IS,inlcuding all labour charges etc., complete of make GM Four Five.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.04 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.04 | day | 1 | day | 615
Labour
Add GHMC Allowance @40%
Labour subtotal
b) Material
|  | 3 | Supply ,Transportation of 4Module 3W LED Foot lamp of make GM Four Five(Approved rate from MRC Qtrs) | 1 | No | 1 | No | 545
Cost of Material
Total Cost of Material + Labour Charges
Rounded of Rate
3W LED light passolite
Data 42
42 | 24-25 RSD 8.1.1 |  | Supply ,Transportation and fixing of 3W LED light passolite as desired by the department and as per IS,inlcuding all labour charges etc., complete
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.04 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.04 | day | 1 | day | 615
Labour
Add GHMC Allowance @40%
Labour subtotal
b) Material
| AR | 3 | Supply ,Transportation of 3W LED Passolite (Approved rate from MRC Qtrs) | 1 | No | 1 | No | 375
Cost of Material
Total Cost of Material + Labour Charges
Rounded of Rate
LED Strip 28W
Data43
43 | 24-25 RSD 8.1.2 |  | Supply ,Transportation and fixing of LED Strip 28W 5mtrs Lenth philips as desired by the department and as per IS,inlcuding all labour charges etc., complete
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.05 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.05 | day | 1 | day | 615
Labour
Add GHMC Allowance @40%
Labour subtotal
b) Material
| AR | 3 | Supply of LED Strp 28W 5mtrs Lenth of make philips (Approved rate from MRC Qtrs) | 5 | Mtrs | 5 | Mtrs | 1375
Cost of Material
Total Cost of Material + Labour Charges
Rounded of Rate
4 Way VTPN DB
Data-44
44 | 24-25 RSD 4.4.8 |  | Supply and fixing of 4 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No 125A ,3 Pole MCCB, 25KA with , 12 Nos 6-32A SP, 10KA , C/D Curve ISI Marked MCBs including connections, terminations glands, lugs and labour charges for SurfaceMounting etc., complete DBMakes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree Xpro. Isolator Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | MATERIAL | Quantity |  | Unit |  | Rate | Amount
| ELEC-2.16.3a | 1 | Supply of 4 Way VTPN DB with IP 43 Protection as per IS:13032 and suitable for accommodating T.P. / S.P. as out goings and 125A / 160A 4 pole MCCB as Incommer etc complete.
|  |  | Makes : Legrand / Schneider / Siemens / LK (L&T) / Hager / Crabtree Xpro / BCH | 1 | No | 1 | No | 15830
| ELEC-2.13.1-a | 2 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark. | 12 | No | 1 | No | 325
Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / LK (L&T) Exora / Crabtree / Indo Asian / BCH
| ELEC-2.7.1-c | 3 | Supply of 125A , 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25KA with thermal magnetic release Panel Mounted of makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/ C&S -Winbreak / BCH | 1 | No | 1 | No | 11380
Cost of Material for 1 No
LABOUR
|  | 4 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 735
|  | 5 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 6 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
COST OF LABOUR
Add GHMC Allowance @40%
Labour Sub total
cost of material +Labour
Rounded off rate
Independent earthing
Data-45
45 |  |  | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II)
|  |  |  | Quantity |  | Unit |  | Rate | Amount
| ELEC -8.16.7 | 1 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II). | 1 | Nos | 1 | Nos | 5840
Cost of Finished item
8 SWG GI Wire
Data-46
46 | 24-25 RSD 5.2.5/2 |  | Supply and Run of No.8 SWG G.I wire including cost of all accessories and labour charges etc., complete. (0.104Kgs/1Mtr)
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 580
Labour for 100 Mtrs
Labour for 1 Mtr
Labour Charges
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC -9.3.6 | 2 | Supply aof No.8 SWG G.I wire. | 10.4 | Kgs | 1 | Kg | 108
| ELEC -10.1.4 | 3 | U Nails. | 1.5 | Nos | 100 | Nos | 44
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Rounded off rate
12Way SPN DB
Data-47
47 | 24-25 RSD 4.4.2b |  | Supply and fixing of 12 Way SPN DB with IP 43 Protection as per IS:13032 including Supply and Fixing of 1 No 40A DP Isolator and 10 Nos 6-32A 10kA ISI Marked C/D curve SP MCBs with all connections and labour charges etc., complete for SurfaceMounting . DBMakes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree Xpro. Isolator Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | LABOUR | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 615
|  | 3 | Semi Skilled Mason. | 0.5 | day | 1 | day | 615
|  | 4 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
COST OF LABOUR for 1 no
Add GHMC Allowance @40%
Labour Sub total
MATERIAL
| Elec-10.4.10 | 5 | Cement. | 5 | Kg | 1 | Kg | 9
| ELEC-2.16.1.f | 6 | Supply of 12 Way SPN DB with IP 43 Protection as per IS:13032 and suitable for 4Nos S.P out goings and for 1 No Incommer etc complete.
|  |  | DBMakes : Legrand / Schneider / Siemens / LK / Crabtree Xpro / ABB / C&S / BCH | 1 | Nos | 1 | No | 2660
| ELEC-2.14.1 b | 7 | Supply of 40A DP Isolator of Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / LK (L&T) Exora / Cabtree / Indo Asian / BCH | 1 | Nos | 1 | No | 590
| ELEC-2.13.1.a | 8 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of Makes :Legrand-DX3 / Schneider-Acti9 /Siemens / LK (L&T) Exora / Crabtree / Indo Asian / BCH | 10 | Nos | 1 | No | 325
Cost of Material
Total Cost of Material + Labour Charges
Rounded off rate
Heavy duty long barrel alluminium 70 sq mm lugs
48 | SD15.4.18 |  | Supply and fixing of heavy duty long barrel alluminium lugs confirming to I.Sspecifications suitable for 70sqmm cable etccomplete with nuts, bolts and washers .Makes: DMI / Jainson / Dowels or equivalent make as approved by the department
|  |  |  | Quantity |  | Unit |  | Rate | Amount
| Elec-4.4.2-e | 1 | Supply of heavy duty long barrel alluminium lugs confirming to I.Sspecifications suitable for 70 sqmm cable etccomplete with nuts, bolts and washers.Makes: DMI / Jainson / Dowels or equivalent make as approved by the department | 1 | No | 1 | Each | 60
Material Sub Total Rs.
Labour
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.013 | No | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.013 | No | 1 | day | 615
Labour Sub Total- A Rs.
Add GHMC Allowance @40%
Total
Total Cost of Material + Labour Charges
Final Rate rounded off
Heavy duty long barrel alluminium 35 sq mm lugs
49 | SD15.4.16 |  | Supply and fixing of heavy duty long barrel alluminium lugs confirming to I.Sspecifications suitable for 35 sqmm cable etccomplete with nuts, bolts and washers .Makes: DMI / Jainson / Dowels or equivalent make as approved by the department
|  |  |  | Quantity |  | Unit |  | Rate | Amount
| Elec-4.4.2-c | 1 | Supply of heavy duty long barrel alluminium lugs confirming to I.Sspecifications suitable for35 sqmm cable etccomplete with nuts, bolts and washers.Makes: DMI / Jainson / Dowels or equivalent make as approved by the department | 1 | No | 1 | Each | 50
Material Sub Total Rs.
Labour
|  | 2 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.013 | No | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.013 | No | 1 | day | 615
Labour Sub Total- A Rs.
Add GHMC Allowance @40%
Total
Total Cost of Material + Labour Charges
Final Rate rounded off
Heavy duty long barrel alluminium 16 sq mm lugs
50 | SD 15.4.14 |  | Supply and fixing of heavy duty long barrel alluminium lugs confirming to I.Sspecifications suitable for upto16sqmm cable etccomplete with nuts, bolts and washers .Makes: DMI / Jainson / Dowels or equivalent make as approved by the department
|  |  |  | Quantity |  | Unit |  | Rate | Amount
| Elec-4.4.2-a | 1 | Supply of heavy duty long barrel alluminium lugs confirming to I.Sspecifications suitable for16sqmm cable etccomplete with nuts, bolts and washers.Makes: DMI / Jainson / Dowels or equivalent make as approved by the department | 1 | No | 1 | Each | 35
Material Sub Total Rs.
Labour
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | No | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | No | 1 | day | 615
Labour Sub Total- A Rs.
Add GHMC Allowance @40%
Total
Total Cost of Material + Labour Charges
Final Rate rounded off
Mirror Lights
Data 51
51 | Finished item |  | Supply of 1 x 11W Mirror light with all standard accessories diffuser Makes : G.E. Venture / Phillips / Crompton / Bajaj.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| MR | 1 | Supply of 1 x 11W Mirror light with all standard accessories diffuser Makes : G.E. Venture / Phillips / Crompton / Bajaj. (MR @ SOR 2024-25ELEC-3.6.1) | 1 | Mtrs | 1 | Mtr | 544
Cost of Material
Telephone Cable
Data52
52 | 24-25 RSD 3.1.2 |  | Supply and laying of 2 Pair, 0.5mm telephone copper cable
Cable Makes : Finolex / Delton / Surabi / Polycab .
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| Elec-9.1.1-a | 4 | Supply of 2 Pair, 0.5mm telephone copper cable of makes : Finolex / Delton / Surabi / Polycab. ( SOR 2024-25 ELEC-9.1.1-a) | 100 | Mtrs | 100 | Mtrs | 1155
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Rounded of Rate
IP Based digtal Telephone
53 | Finished Item |  | IP Based digtal Telephone (EPABX) system complied with following specifications: > IP @ Core, PCM/TDM, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console,> Must support Mobile SIP (Android and I O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt 8 Channel Auto Attendant > Inbuilt Call Details Software with search engine software > 4 Analog Trunks > 6 Digital Extensions > 32 Analog Extensions > 1 Digital Key Phone with minimum 16 Keys (Must work only on 2 wires) > Expandable to 64 Analog Extensions or more of Approved Brands: NEC/ Alcatel/ Karel/ Unify.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| Elec-9.3.1 | 1 | IP Based digtal Telephone (EPABX) system complied with following specifications: > IP @ Core, PCM/TDM, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console, > Must support Mobile SIP (Android and I O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt 8 Channel Auto Attendant > Inbuilt Call Details Software with search engine software > 4 Analog Trunks > 6 Digital Extensions > 32 Analog Extensions > 1 Digital Key Phone with minimum 16 Keys (Must work only on 2 wires) > Expandable to 64 Analog Extensions or more Approved Brands: NEC/ Alcatel/ Karel/ Unify. (SOR 2024-25 ELEC-9.3.1) | 1 | No | 1 | No | 130000
Cost of Material for 1 No
Digital Key Telephone with 2 line display
54 |  |  | Digital Key Telephone with 2 line display, 10 programmable keys, handsfree dialing.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.4.13 | 1 | Digital Key Telephone with 2 line display, 10 programmable keys, handsfree dialing. | 1 | No | 1 | No | 13752
Cost of Material for 1 No
50pair Telephone distribution box
55 | SD-NA |  | Supply and installation of 50pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| Elec-9.1.2-c | 1 | Supply of 50pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement. Proportional to (ELEC-9.1.2c) | 1 | No | 1 | No | 2590
Cost of Material for 1 No
| Provisional rate | 2 | a)Labour for installation (derived from agreement approved rate EE(Gl) Agt No.82/2024-25 Dt.09.07.2019 | 1 | Job | 1 | Job | 90
Total Cost of Material + Labour Charges
Rounded off rate
20 pair Telephone distribution box with back mount frame
56 | SD-NA |  | Supply and installation of 20pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| Elec-9.1.2-b | 1 | "Supply of 20pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement. | 1 | No | 1 | No | 1230
Cost of Material for 1 No
| Provisional rate | 2 | a)Labour for installation (derived from agreement approved rate EE(Gl) Agt No.82/2024-25 Dt.09.07.2019 | 1 | Job | 1 | Job | 90
Total Cost of Material + Labour Charges
Rounded off rate
Caller ID Pushbutton
57 | Approved rate |  | Supply and installation of Caller ID Pushbutton Telephone instruments Make: Beetel
| EE(Gl) Agreement rate |  | b) Material | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Supply and installation of Caller ID Pushbutton Telephone instruments Make: Beetel (Approved rate from MRC Qtrs) | 1 | No | 1 | No | 637
Cost of Material for 1 No
2Port Line Protection
58 | Approved rate |  | Supply and installation of 2Port Line Protection Unit of Make: Crystla
| EE(Gl) Agreement rate |  | b) Material | Quantity |  | Unit |  | Rate | Amount
|  |  | Supply and installation of 2Port Line Protection Unit of Make: Crystla (Approved rate from MRC Qtrs) | 1 | No | 1 | No | 1200
Cost of Material for 1 No
600 mm width x 500 mm net work rack
59 | Finished item |  | Supply and installation of …… 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilevershelf etc., complete. Makes : Vallrack (Legrand) / Netrack.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.1.15b | 1 | Supply and installation of …… 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK 08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilevershelf etc., complete. Makes : Vallrack (Legrand) / Netrack. | 1 | No | 1 | No | 8385
Cost of Material for 1 No
Modular telephone Jack with connector
60 | 24-25 RSD 2.1.4 |  | supply and fixing of Modular telephone Jack with connector on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.a | 3 | Supply of 1 or 2 Module box | 1 | Nos | 1 | No | 80
| ELEC-1.3.3.a | 4 | Supply of 1 or 2 Modular Cover Frame.
|  |  | Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana | 1 | Nos | 1 | No | 75
| ELEC-1.9.2.o | 5 | Supply of Modular socket type Telephone jack with Connector.
|  |  | Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus/ Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / SalzarElite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 90
Total material cost
Total Material and Labour charges for 1 no
Rounded off rate
LAN Cable cat - 6 UTP cable
61 | Finished item |  | Supply of LAN Cable cat - 6 UTP cable. Makes : D Link / AMP / Molex / Legrand / Krone.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.1.3A | 1 | Supply of LAN Cable cat - 6 UTP cable. Makes : D Link / AMP / Molex / Legrand / Krone. | 100 | Mtrs | 100 | Mtrs | 2920
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
8 Port D-Link Desktop Switch
62 | Finished item |  | Supply and fixing of 8 Port D-Link DGS-1008A 8-Port Gigabit Easy Desktop Switch (White) of Makes : D link including all connections.
b) Material
| AR | 1 | Supply and fixing of 8 Port D-Link DGS-1008A 8-Port Gigabit Easy Desktop Switch (White) of Makes : D link including all connections. (Approved rate from MRC Qtrs) | 1 | Nos | 1 | Nos | 2391
Cost of Material
Rounded off rate
3 feet length moulded patch cord
63 | Finished item |  | Supply of 3 feet length moulded patch cord. Makes : D Link / AMP / Molex / Legrand / Krone.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.1.10b | 1 | Supply of 3 feet length moulded patch cord. Makes : D Link / AMP / Molex / Legrand | 1 | Nos | 1 | Nos | 175
Cost of Material
Rounded off rate
Wireless-N300 Routewith RJ 45 Jacks
64 | Finished item |  | Supply and fixing of access point D-Link DIR-615 Wireless-N300 Router including gicing connections and cable terminations with RJ 45 Jacks crimiping etc complete.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| AR | 1 | Supply and fixing of access point D-Link DIR-615 Wireless-N300 Router including gicing connections and cable terminations with RJ 45 Jacks crimiping etc complete. (Approved rate from MRC Qtrs) | 1 | Nos | 1 | Nos | 1330
Cost of Material
Rounded off rate
600 mm width x 500 mm network Rack
65 | Finished item |  | Supply and installation of …… 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilever shelf etc.,complete. Makes : Vallrack (Legrand) / Netrack.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.1.15-a | 1 | Supply and installation of …… 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilever shelf etc.,complete. Makes : Vallrack (Legrand) / Netrack. | 1 | No | 1 | No | 7040
Cost of Material for 1 No
RG-6 Cu flexible cable
66 | NA SD |  | Supply and Run of 1 of RG-6 Cu flexible ISI mark coaxial foarmed cable in existing pipe for TV's inlcuding all labour charges etc., complete of make Finolex/ RR Kable
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| Pricelist | 4 | Supply of of 1 of RG-6 Cu flexible ISI mark coaxial foarmed cable make Finolex/ RR Kable (Approved rate from MRC Qtrs) | 100 | Mtrs | 1 | Mtrs | 22
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Rounded of Rate
Cat 6 RJ 45 Outlet
67 | 24-25 RSD 2.1.4 |  | Supply and fixing of Cat 6 RJ-45 information outlets including -single face plate on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : D Link / AMP / Molex / Legrand / Krone.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| Elec-1.3.1-a | 3 | Supply of 1 or 2 Module box. | 1 | Nos | 1 | No | 80
| ELEC-1.3.4.a | 4 | Supply of 1 or 2 Modular Cover Frame
|  |  | Makes :Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Crabtree Murano / Logus Platina / Gold Medal GIFA / GM-Zenova/ LK (L&T) Englaze / Million M-Vee | 1 | Nos | 1 | No | 75
| ELEC-9.1.5.b | 5 | Supply of Cat 6 RJ-45 information outlets including -Single face plate of Makes : D Link / AMP / Molex / Legrand / Krone. | 1 | Nos | 1 | No | 290
Total material cost
Total Material and Labour charges for 1 no
Rounded off rate
TV Socket
68 | 24-25 RSD 2.1.4 |  | Supply and fixing of Modular co-Axial socket type TV Antenna outlet on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.a | 3 | Supply of 1 or 2 Module box. SOR-2024-25 | 1 | Nos | 1 | No | 80
|  | 4 | Supply of 1 or 2 Modular Cover Frame.SOR-2024-25()
| ELEC-1.3.4.a |  | Makes : Legrand Myrius / Million Tap-Wood / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana | 1 | Nos | 1 | No | 75
| ELEC-1.9.2 p | 5 | Supply of Modular co-Axial socket type TV Antenna outlet. Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus/ Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / SalzarElite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 85
Total material cost
Total Material and Labour charges for 1 no
Rounded off rate
2.0/1.8 TR Split AC's
Data 69
69 | NA-SD |  | Supply,Installation testing and commissioning of INVERTER Model Cool type split AC unit 2.0 / 1.8 TR 5 Star capable of delivering 21600 BTU/hr and above with operating on refrigerant R-32 / R-410 Makes : Daikin / Toshibha / Carrier / Blue Star / Hitachi or equivalent with high wall mounted Single Split indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing Heat cool dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 4 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with warranty of compressor for 5 years including MS bracket / MS angle iron stand with pads suitable for fixing out door unit of split AC unit with Warranty and CMC for Two years.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-6.1.1-d | 1 |  | 1 | Nos | 1 | Nos | 54000
| ELEC-6.7.28 | 2 | Installation of Split Air Conditioners. | 1 | Nos | 1 | Nos | 1760
| ELEC-6.7.1 | 3 | Supply, Fabrication of 1set MS bracket suitable for fixing out door unit of split AC Unit. | 1 | Nos | 1 | Nos | 914
Cost & installation of Unit
Rounded off rate
1.5 TR Split AC's
Data 70
70 | NA-SD |  | Supply,Installation testing and commissioning of INVERTER Model Cool type split AC unit 1.5 TR 5 Star capable of delivering 18000 BTU/hr and above with operating on refrigerant R-32 / R-410 Makes : Daikin / Toshibha / Carrier / Blue Star / Hitachi or equivalent with high wall mounted Single Split indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing Heat cool dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 4 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with warranty of compressor for 5 years including MS bracket / MS angle iron stand with pads suitable for fixing out door unit of split AC unit with Warranty and CMC for Two years.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-6.2.1-b | 1 |  | 1 | Nos | 1 | Nos | 41992
| ELEC-6.7.28 | 2 | Installation of Split Air Conditioners. | 1 | Nos | 1 | Nos | 1680
| ELEC-6.7.1 | 3 | Supply, Fabrication of 1set MS bracket suitable for fixing out door unit of split AC Unit. | 1 | Nos | 1 | Nos | 960
Cost & installation of Unit
Rounded off rate
Copper Pipe
Data 71
71 | Finished item |  | Providing Additional 2 runs of 3/4" x 3/8" or 5/8" x 1/4" or 1/2"x 1/4" Copper tubes for suction and liquid between indoor and outdoor unit suitable size for Split Air-Conditioner including foaming, wrapping etc.,complete
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-6.7.2-a | 1 | Providing Additional 2 runs of 3/4" x 3/8" or 5/8" x 1/4" or 1/2"x 1/4" Copper tubes for suction and liquid between indoor and outdoor unit suitable size for Split Air-Conditioner including foaming, wrapping etc.,complete. | 1 | Nos | 1 | Nos | 990
Cost of Material
|  |  | Rounded off rate | [5 empty] | 943
3core 2.5 Sqmm
Data 72
72 | 25 Sqmm Laying Half Labour Charges |  | Supply and laying of 2.5 Sqmm ( ) 3 Core PVC Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS:694:1990 including all transportation charges etc complete.Makes : Finolex / RR kabel / Havells / Polycab/ RPG.
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
Labour Charges for 100 Mtrs
Labour Charges for 1 Mtr
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC-1.5.6-n | 3 | Supply of 2.5 Sqmm 3 Core PVC Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS:694:1990 including all transportation charges etc complete.Makes : Finolex / RR kabel / Havells / Polycab/ RPG / Gloster /KEI/V- Guard. | 1 | Nos | 1 | Nos | 135
Cost of Material
Total Material and Labour charges for 1 mts
Rounded off rate
CPVC Pipe
Data 73
73 | Finished item |  | Supply, installation, testing and commissioning of the drain line with CPVC pipes of premium make of 28.60mm OD Pipe- SDR 13.5.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| TBSP-J.III-03 | 1 | Supply of premium make CPVC Pipes of 28.60mm OD Pipe- SDR 13.5. | 1 | Nos | 1 | Nos | 235
Cost of Material
Rounded off rate
Core Cutting
Data 74
74 |  |  | Making core cutting to existing wall and chipping to the existing wall for providing drain piping and copper piping for providing new air conditioners units including all labour charges etc complete.
b) Material
| Approved rate | 1 | Making core cutting to existing wall and chipping to the existing wall for providing drain piping and copper piping for providing new air conditioners units including all labour charges etc complete. (Approved Rate MRC Qtr No 4) | 1 | Nos | 1 | Nos | 550
Cost of Material
Rounded off rate
1.00 HP Open Well Motor
Data 75
75 | Finished item |  | Supply,Transportation and fixing of 1.00HP Single phase open well ISI submersible motor pumpset of make Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-5.7.1-a | 1 | Supply,Transportation and fixing of 1.00HP Single phase open well ISI submersible motor pumpset of make Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon | 1 | Nos | 1 | Nos | 17000
Cost of Material
Rounded off rate
Control Panel
Data 76
76 | Finished item |  | Supply, Transportation and Fixing of control panel for single phase submersible motors up to 3 HP @ 220V 50Hz operating range between 80 to 240V including supply and fixing of Direct - on - Line LTLK / SIEMENS / CROMPTON make Volt meter and Ammeter with starting and running capacitors assembled with ISI mark contactors and fitted with Legrand make ISI mark MCB etc., complete.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-5.10.1 | 1 | Supply, Transportation and Fixing of control panel for single phase submersible motors up to 3 HP @ 220V 50Hz operating range between 80 to 240V including supply and fixing of Direct - on - Line LTLK / SIEMENS / CROMPTON make Volt meter and Ammeter with starting and running capacitors assembled with ISI mark contactors and fitted with Legrand make ISI mark MCB etc., complete. | 1 | Nos | 1 | Nos | 9750
Cost of Material
Rounded off rate
25mm GI Pipe
Data 77
77 | Finished item |  | Supply and fixing of 25mm Nominal Bore GI pipe Medium Grade properties & weight as per IS 1239 ISI mark with GI fittings including the cost of pipe, Nipples, bends,Elbows & its fittings & labour charges complete of Makes : Zoloto / Leader / Approved makes
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| TBSP-G.I-09 | 1 | Supply and fixing of 25mm Nominal Bore GI pipe Medium Grade properties & weight as per IS 1239 ISI mark with GI fittings including the cost of pipe, Nipples, bends,Elbows & its fittings & labour charges complete of Makes : Zoloto / Leader / Approved makes. | 1 | Nos | 1 | Nos | 326
Cost of Material
Rounded off rate
25mm Gate Valve
Data 78
78 | Finished item |  | Supply, installation, testing and commissioning of 25mm dia Gate valve of Makes : Zoloto / Leader /Approved makes.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-10.7.39 | 1 | Supplying, installing, testing and commissioning of Forged brass chrome finished Ball valves with fittings of screwed end type of makes : Zoloto / Leader / Honeywell / Kartar. | 1 | Nos | 1 | Nos | 1392
Cost of Material
Rounded off rate
3 Core 4.0 Sqmm Flat Copper Cable
Data 79
79 |  |  | Supply and laying of 3 Core 4.0 Sqmm Flat Copper cable of ISI for Submersible Motors of Makes : Finolex / RR Kabel / Havells / KEI /L&T including all labour charges etc complete.
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
| 25 Sqmm Laying Half Labour Charges | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
Labour Charges for 100 Mtrs
Labour Charges for 1 Mtr
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC-1.6.3-c | 3 | Supply of 3 Core 4.0 Sqmm Flat Copper cable of ISI for Submersible Motors of Makes : Finolex / RR Kabel / Havells / KEI / LK (L&T) / Pawancab | 1 | Mts | 100 | Mtr | 18530
Cost of Material
Total Material and Labour charges for 1 mts
Rounded off rate
Water Dispenser
Data 80
80 | Finished item |  | Supply, Transporatation and Installation of water dispenser Voltas Mini magic, Hot, cold and normal including 24 months warranty, AMC etc., complete.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| AR | 1 | Supply, Transporatation and Installation of water dispenser Voltas Mini magic, Hot, cold and normal including 24 months warranty, AMC etc., complete. (Approved rate from MRC Qtrs) | 1 | Nos | 1 | Nos | 11700
Cost of Material
Rounded off rate
Water Purifier
Data 81
81 | Finished item |  | Supply, Transporatation and Installation of Kent Water Purifier 8L RO+UV+UF model, Grand Plus as per the direction of dept engineer including 24 months warranty, AMC etc., complete
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| AR | 1 | Supply, Transporatation and Installation of Kent Water Purifier 8L RO+UV+UF model, Grand Plus as per the direction of dept engineer including 24 months warranty, AMC etc., complete (Approved rate from MRC Qtrs) | 1 | Nos | 1 | Nos | 23000
Cost of Material
Rounded off rate
40 KVA DG Set
Data 82
82 | Finished item |  | Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 40 KVA/32 KW out put contineous rating directly coupled Engine and Alternator with guard and mounted on a common base plate of Robust construction and complete with standard control panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, to restrict sound level up to 75 dB up to 1 mtr distance and as per CPCB norms etc as per following specifications mentioned below.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-12.1.1-f | 1 | Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 40 KVA/32 KW out put contineous rating directly coupled Engine and Alternator with guard and mounted on a common base plate of Robust construction and complete with standard control panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, to restrict sound level up to 75 dB up to 1 mtr distance and as per CPCB norms etc as per following specifications mentioned below. | 1 | Nos | 1 | Nos | 713000
Cost of Material
Rounded off rate
125A 4 Pole Changeover
Data 83
83 | Finished item |  | Supply and fixing of 125A 4 Pole Change Over Switch on Load with open Execution of Makes : Socomec / L & T .
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-2.2.1-b | 1 | Supply of 125A 4 Pole Change Over Switch on Load with open Execution. Makes : Socomec / L & T. | 1 | Nos | 1 | Nos | 11850
Cost of Material
Rounded off rate
125A 4 Pole MCCB
Data 84
84 | Finished item |  | Supply and fixing of 125A 4 Pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16KA with thermal magnetic release with enclosure of Makes : L&T / Schneider / Siemens / Legrand / Hager / ABB
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-2.7.1-d | 1 | Supply and fixing of 125A 4 Pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16KA with thermal magnetic release with enclosure of Makes : L&T / Schneider / Siemens / Legrand / Hager / ABB. | 1 | Nos | 1 | Nos | 13770
Cost of Material
Rounded off rate
Independent Copper earthing
Data-85
85 |  |  | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 19mm dia 'B' Class G.I Pipe of 2.5Mtr lengthwith funnel as per National Electric Code and earth connection from electrode GI strip of 40mm x 5mm x 200mm length to be bolted with nut bolts to G.I.pipe including 25mm x 3mm copper strip of 6Mtrs length connected from plate to GI strip including filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe and providing CC / Brick massonry chamber 450mmX450mmX400mm and covered with R.C.C. Slab including all accessories and labour charges etc complete as per IS specification 732/1982 (Part II).
| ELEC -8.16.8 | 1 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 19mm dia 'B' Class G.I Pipe of 2.5Mtr lengthwith funnel as per National Electric Code and earth connection from electrode GI strip of 40mm x 5mm x 200mm length to be bolted with nut bolts to G.I.pipe including 25mm x 3mm copper strip of 6Mtrs length connected from plate to GI strip including filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe and providing CC / Brick massonry chamber 450mmX450mmX400mm and covered with R.C.C. Slab including all accessories and labour charges etc complete as per IS specification 732/1982 (Part II). | 1 | Nos | 1 | Nos | 16670
Cost of Finished item
Independent GI earthing
Data-86
86 |  |  | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II)
| ELEC -7.16.7 | 1 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II). | 1 | Nos | 1 | Nos | 5840
Cost of Finished item
GI Strip
Data 87
87 | 24-25-27.1.7 |  | Supply and Run of 50mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. (2.36Kgs/1Mtr) (SD 5.2.7)
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
Labour for 100 Mtrs
Labour for 1 Mtr
b) Material
| ELEC -10.3.6 | 3 | G.I. Strip / Plate / Wire (per K. G). | 236 | Kgs | 1 | Kg | 108
|  | 4 | Sundries.
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Copper Strip
Data 88
88 | 24-25-28.1.11 |  | Supply and Run of 25mm x 6mm copper strip (Cuurrent Carrying Capacity 350A) including cost of all accessories and labour charges etc., complete. (1.34Kgs/1Mtr)(SD 5.3.5)
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 2 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
Labour for 100 Mtrs
Labour for 1 Mtr
b) Material
| ELEC -10.3.1 | 3 | Copper plate / Copper strip (Per K.G). | 134 | Kgs | 1 | Kg | 1148
|  | 4 | Sundries.
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
4 Passeneger Lift
89 |  |  | Supply, transportation,installation and commissioning of 4 passenger hydraulic passenger elevator with following specifications including required accessories and with all civil works required for installation of lift at staircase area.Make:MAHA LIFTS or its eqivalent,
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| Finished item | 1 | Supply, transportation,installation and commissioning of 4 passenger hydraulic passenger elevator with following specifications including required accessories and with all civil works required for installation of lift at staircase area.Make:MAHA LIFTS or its eqivalent, (Approved rate from | 1 | Nos | 1 | Nos | 1450000
1.Capacity: 272 Kgs(4 persons)
2.Type of Lift :Passenger Lift,
3.Power requirement : a) Main Supply: 415 V, Three phase 50Hz A.C duly earthed b) Aux. Supply: 230 V, Single phase A.C. duly earthed
4.Speed:0.3Mts/Sec,
5.Travel distance : 6.6Mts (G + 2 Floors)
6. Type of drive : Electronically controlled hydraulic drive
7.Location of Power Unit :Near the lift shaft in ground floor
8. Key Civil Dimensions of Lift Shaft : 1500 (W) X 1500 (D) Bottom pit required: 300 mm min
9. Passenger Cabin Dimensions : 1000 mm (W) X 1000 mm (D) X 2200 mm (H)
10.Passenger Cabin Interiors a) Panels: S.S.304 b) False Ceiling: Same as Panels with one Fan and 4 LED lights c) Flooring: Anti-Skid PVC d) Operating Panel: SS Finish with digital position indicators and call registration light in all buttons. Other than the floor buttons the panel will also have buttons for emergency stop, on-off operation of fan and on-off operation of cabin light
11.Clear Door Opening: 700 mm (W) X 2000 mm (H)
12.Type of Doors : a) cabin door: Infrared sensor, b) landing doors: UPVC Swing Door / M.S. Powder coated big vision glass doors
13.Safety Provisions: a) Automatic positioning of lift to ground floor in case of power failure b) Door safeties (Lift shall not operate if door(s) are open and door(s) will not open if lift is in operation) c) Door locks d) Hose burst valve e) Rope slack valve to prevent internal leakage f) Emergency Alarm g) Emergency Cabin Light Heavy duty structure
14.Hydraulic System: Hydraulic System: a) Hydraulic Oil Tank Capacity : 100 litres b) Oil Tank Material :MS Structure welded and painted, c) Control Valves : Blain, Germany d) Safety valves : Blain, Germany e) Motor : 5 HP Crompton Greeves / scimens, f) Pump : SIEM g) Cylinder : Our own make h) No. of Cylinders : 1 No i) Tube : ST-52 j) Piston Rod : 90 mm Dia. CK-45 with hard chrome plating up to 25-30 micron thickness
16.Structural support for guide rails :100 mm square tubes
17.Guide Rails :10 mm Heavy Duty
18.Controller :PLC based controller
Cost of Material
|  |  | Rounded off rate | [5 empty] | 1450000
Telephone Cable
Data 91
90 | 24-25 RSD 3.1.2 |  | Supply and laying of 2 Pair, 0.5mm telephone copper cable
Cable Makes : Finolex / Delton / Surabi / Polycab .
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| Elec-9.1.1-a | 4 | Supply of 2 Pair, 0.5mm telephone copper cable of makes : Finolex / Delton / Surabi / Polycab. ( SOR 2024-25 ELEC-9.1.1-a) | 100 | Mtrs | 100 | Mtrs | 1155
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
20Pair Telephone Distribution Box
Data 91
91 | SD-NA |  | Supply and installation of 20pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| Elec-9.1.2-b | 1 | "Supply of 20pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement. | 1 | No | 1 | No | 1230
Cost of Material for 1 No
| Provisional rate | 2 | a)Labour for installation (derived from agreement approved rate EE(Gl) Agt No.82/2024-25 Dt.09.07.2019 | 1 | Job | 1 | Job | 90
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Modular Telephone Jack
Data-92
92 | 24-25 RSD 2.1.4 |  | supply and fixing of Modular telephone Jack with connector on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.a | 3 | Supply of 1 or 2 Module box Similar to Switches Make | 1 | Nos | 1 | No | 80
| ELEC-1.3.3.a | 4 | Supply of 1 or 2 Modular Cover Frame.
|  |  | Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 85
| ELEC-1.9.2.o | 5 | Supply of Modular socket type Telephone jack with Connector.
|  |  | Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 90
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
LAN Cable CAT-6 UTP
Data-93
93 | Finished item |  | Supply of LAN Cable cat - 6 UTP cable of Makes : D Link / AMP / Molex / Legrand / Krone.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.1.3 a | 1 | Supply of LAN Cable cat - 6 UTP cable. Makes : D Link / AMP / Molex / Legrand / Krone. | 100 | Mtrs | 100 | Mtrs | 2920
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Add Overhead @ 10.615%
Total Rate
Rounded off rate
8 Port D-Link DGS-1008A 8-Port Gigabit Switch
94 |  |  | Data 94
| Finished item |  | Supply and fixing of 8 Port D-Link DGS-1008A 8-Port Gigabit Easy Desktop Switch (White) of Makes : D link including all connections.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| Elec-9.1.7-c | 1 | Supply of 8 Port 10 / 100 / 1000 Gigabit Unmanageable Ethernet switch. Makes : TP Link / D link / Netfox. | 1 | Nos | 1 | Nos | 2180
Cost of Material
Add Overhead @ 10.615%
Total Rate
Rounded off rate
3 feet length moulded patch cord
Data 95
95 | Finished item |  | Supply of 3 feet length moulded patch cord. Makes : D Link / AMP / Molex / Legrand / Krone.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.1.10-b | 1 | Supply of 3 feet length moulded patch cord. Makes : D Link / AMP / Molex / Legrand / Krone. | 1 | Nos | 1 | Nos | 175
Cost of Material
Add Overhead @ 10.615%
Total Rate
Rounded off rate
D-Link DIR-615 Wireless-N300 Router
Data 96
96 | Finished item |  | Supply and fixing of access point D-Link DIR-615 Wireless-N300 Router including gicing connections and cable terminations with RJ 45 Jacks crimiping etc complete.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| AR | 1 | Supply and fixing of access point D-Link DIR-615 Wireless-N300 Router including gicing connections and cable terminations with RJ 45 Jacks crimiping etc complete. (Approved rate from MRC Qtrs) | 1 | Nos | 1 | Nos | 1330
Cost of Material
Rounded off rate
6U Wall mounting Rack
Data 97
97 | Finished item |  | Supply and installation of 6U Wall Rack 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK 08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilever shelf etc., complete. Makes : Vallrack (Legrand) / Netrack.
|  |  | b) Material | Quantity |  | Unit |  | Rate | Amount
| ELEC-9.1.15-a | 1 | Supply and installation of 6U Wall Rack 600 mm width x 500 mm depth UL certified wall mounting net work rack with sheet steel revited metal frame, top and bottom cover with brush cable entry, confirming to following standards IEC 60529, EN 60529 ( IP 20), IEC 62262 EN 62622 (IK 08) , DIN 41494, EIA 310, IEC 60927 including all accessories like horizontal PDU, metal cable manager, hardware packet and the cantilever shelf etc., complete. Makes : Vallrack (Legrand) / Netrack. | 1 | No | 1 | No | 7040
Cost of Material for 1 No
Add Overhead @ 10.615%
Total Rate
Rounded off rate
RG-6 Cu flexible cable
Data 98
98 | NA SD |  | Supply and Run of 1 of RG-6 Cu flexible ISI mark coaxial foarmed cable in existing pipe for TV's inlcuding all labour charges etc., complete of make Finolex/ RR Kable
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.34 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.34 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| Pricelist | 4 | Supply of of 1 of RG-6 Cu flexible ISI mark coaxial foarmed cable make Finolex/ RR Kable (Approved rate from MRC Qtrs) | 100 | Mtrs | 1 | Mtrs | 22
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Cat 6 RJ-45 information outlets
Data-99
99 | 24-25 RSD 2.1.4 |  | Supply and fixing of Cat 6 RJ-45 information outlets including -single face plate on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : D Link / AMP / Molex / Legrand / Krone.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2020-21 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 590
|  | 2 | Helper. SOR-2020-21 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 490
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.a | 3 | Supply of 1 or 2 Module box Similar to Switches Make | 1 | Nos | 1 | No | 59
| ELEC-1.3.3.a | 4 | Supply of 1 or 2 Modular Cover Frame.
|  |  | Makes : Legrand Myrius / Million Tap-Wood / Anchor Roma viola / Havells Fabio / C&S Prime / CPL Vysma / Benlo Vesta / Polycab Levana | 1 | Nos | 1 | No | 58
| ELEC-8.1.4.b | 5 | Supply of Cat 6 RJ-45 information outlets including -Single face plate of Makes : D Link / AMP / Molex / Legrand / Krone. | 1 | Nos | 1 | No | 230
Total material cost
Total Material and Labour charges for 1 no
Total Rate
Rounded off rate
Modular co-Axial socket type TV Antenna outlet
Data-100
100 | 24-25 RSD 2.1.4 |  | Supply and fixing of Modular co-Axial socket type TV Antenna outlet on modular box with cover frame in existing surface / consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in R.B Makes : Legrand Myrius / Million mway / Gold Medal Curve / Anchor Roma viola / GM Four-Five / Havells Fabio / Panasonic Vision / L&T Englaze / Hager Insista / Benlo Vesta / C&S Primo / CPL Vysma / Polycab Levana.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.033 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.a | 3 | Supply of 1 or 2 Module box Similar to Switches Make | 1 | Nos | 1 | No | 80
| ELEC-1.3.4.a | 4 | Supply of 1 or 2 Modular Cover Frame.
|  |  | Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 75
| ELEC-1.9.2 p | 5 | Supply of Modular co-Axial socket type TV Antenna outlet. Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 85
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
LED Bulbs
Data 101
101 | 24-25 RSD 4.4.4A |  | Supply of 12.0W LED Lamp with input voltage 90 to 300V, Colour temparature 3000k- 6500k, Beam angle 170 - 220 °C, B22 base. Makes: Phillips / OSRAM / Crompton / Eveready / Bajaj / Havells / Pharox / Halonix / Greenlites / IB LED/ Jaquar / C&S / GM / FIEM / Gold Medal / Million / Syska.
DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | a) Labour charges for Flush Mounting | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-3.4.1-f | 7 | Supply of 12.0W LED Lamp with input voltage 90 to 300V, Colour temparature 3000k- 6500k, Beam angle 170 - 220 °C, B22 base. Makes: Phillips / OSRAM / Crompton / Eveready / Bajaj / Havells / Pharox / Halonix / Greenlites / IB LED/ Jaquar / C&S / GM / FIEM / Gold Medal / Million / Syska. | 1 | Nos | 1 | No | 170
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Batten Holders
Data 102
102 | 24-25 RSD 4.4.4A |  | Supply of MC Holder Makes : GM / Million / Gold Medal / Anchor /Great white.
DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | a) Labour charges for Flush Mounting | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-1.7.2 e | 7 | Supply of MC Holder Makes : GM / Million / Gold Medal / Anchor /Great white. | 1 | Nos | 1 | No | 25
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
2Module boxes with cover frame
Data-103
103 | 24-25-RSD 2.1.2 |  | Supply of 2 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. and Supply of 2 Module box similar to switch make.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour Rate for 1 board
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.a | 7 | Supply of 2 Module box similar to switch make. | 1 | Nos | 1 | No | 80
| ELEC-1.3.4.a | 9 | Supply of 2 Modular Cover Frame of makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. | 1 | Nos | 1 | No | 75
Total material cost for 1 board
Total Material and Labour charges for 1 pt
Add Overhead @ 10.615%
Total Rate
Rounded off rate
3 Modular switch boards with cover frame
Data-104
104 | 24-25-RSD 2.1.2 | 22-23-RSD2.1.2 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X and supply of 3 module box similar switch make
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour Rate for 1 pt
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.b | 6 | Supply of 3 Module box similar to switch make. | 1 | Nos | 1 | No | 110
| ELEC-1.3.4.b | 8 | Supply of 3 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 95
Total material cost for 1 board
Total Material and Labour charges for 1 board
Add Overhead @ 10.615%
Total Rate
Rounded off rate
4 Module boxes with cover frame
Data-105
105 | 24-25-RSD 2.1.2 |  | Supply of 4 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. and Supply of 4 Module box similar to switch make.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour Rate for 1 board
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.c | 7 | Supply of 4 Module box similar to switch make. | 1 | Nos | 1 | No | 130
| ELEC-1.3.4.c | 9 | Supply of 4 Modular Cover Frame of makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. | 1 | Nos | 1 | No | 110
Total material cost for 1 board
Total Material and Labour charges for 1 pt
Add Overhead @ 10.615%
Total Rate
Rounded off rate
6 Modular switch boards with cover frame
Data-106
106 | 24-25 RSD 2.1.6X2 |  | Supply of 6 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. and Supply of 6 Module box similar to switch make.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.d | 4 | Supply of 6 Module box similar to switch make. | 1 | Nos | 1 | No | 180
| ELEC-1.3.4.d | 5 | Supply of 6 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. | 1 | Nos | 1 | No | 150
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
8Module boxes with cover frame
Data-107
107 | 24-25 RSD 2.1.4X3 |  | Supply of 8 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. and Supply of 8 Module box similar to switch make.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.e | 3 | Supply of 8/9 Horizontal/Vertical Module box similar to switches make. | 1 | Nos | 1 | No | 235
| ELEC-1.3.4.e | 4 | Supply of 8 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 185
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
12 Module switch boards with cover frame
Data-108
108 | 24-25 RSD 2.1.4X4 |  | Supply of 12 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. and Supply of 12 Module box similar to switch make.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.f | 3 | Supply of 12 Module box similar to switch make. | 1 | Nos | 1 | No | 285
| ELEC-1.3.4.f | 4 | Supply of 12 Modular Cover Frame of Makes :Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus/ Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 230
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
18 Module boxes with cover frame
Data 109
109 | 24-25-RSD 2.1.2 |  | Supply of 18 Modular Cover Frame of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. and Supply of 18 Module box similar to switch make.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour Rate for 1 board
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.3.1.a | 7 | Supply of 18Module box similar to switch make. | 1 | Nos | 1 | No | 365
| ELEC-1.3.4.h | 9 | Supply of 18 Modular Cover Frame of makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. | 1 | Nos | 1 | No | 290
Total material cost for 1 board
Total Material and Labour charges for 1 pt
Add Overhead @ 10.615%
Total Rate
Rounded off rate
10A 3/2 Pin 2 Module Modular Socket with shutter.
Data-110
110 | 24-25 RSD 2.1.6 |  | Supply and fixing of ISI marked 10A 3/2 Pin 2 Module Modular Socket with shutter., complete in N.R.B. / R.B. Makes :: Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.d | 6 | Supply and fixing of ISI marked 10A 3/2 Pin 2 Module Modular Socket with shutter., complete in N.R.B. / R.B. Makes :: Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. | 1 | Nos | 1 | No | 125
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
16A sockets
Data-111
111 | 24-25 RSD 2.1.6 |  | Supply and fixing of ISI marked16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter., complete in N.R.B. / R.B. Makes :: Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X.
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.i | 6 | Supply and fixing of ISI marked16A / 6A 1 way 2 Module Combi Socket Modular Socket with shutter., complete in N.R.B. / R.B. Makes :: Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X. | 1 | Nos | 1 | No | 180
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
6/10 switches
Data-112
112 | 24-25 RSD 2.1.4 |  | Supply and fixing of ISI Marked 6/10A 1way Modular switch including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.a | 6 | Supply and fixing of ISI Marked 6/10A 1way Modular switch including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 85
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
16/20 switches
Data-113
113 | 24-25 RSD 2.1.4 |  | Supply and fixing of ISI Marked 16/20A 1way Modular switch including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.h | 6 | Supply and fixing of ISI Marked 16/20A 1way Modular switch including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 110
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
63A FP Isolators
Data 114
114 | 24-25 RSD 4.4.4A |  | Supply of 63A FP Isolator of Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree / Indo Asian / BCH .
DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | a) Labour charges for Flush Mounting | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-2.14.1-g | 7 | Supply of 63A FP Isolator of Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree / Indo Asian / BCH . | 1 | Nos | 1 | No | 1440
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
6-32A MCBs
Data 115
115 | 24-25 RSD 4.4.4A |  | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree / Indo Asian / BCH.
DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | a) Labour charges for Flush Mounting | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-2.13.1 -a | 8 | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark of make Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree / Indo Asian / BCH. | 1 | Nos | 1 | No | 325
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Water Geyser
Data 116
116 | 24-25 RSD 4.4.4A |  | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type Vertical / Horizontal 230/250V single phase 2000 watts 5 Star rated water heater with ABS plastic body of capacity to withstand up to 8.0 bar of water pressure including all standard accessories and dead weight pressure reducing valve on out let side, including cost of 2 Nos SS flexible braided hose pipe, testing and all labour charges etc., complete. Makes : Crompton / Jaquar / Venus / Racold / AO Smith / Havells / Bajaj or equivalent as approved by the Dept.
DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | a) Labour charges for Flush Mounting | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.2 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.1 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-5.2.1-c | 7 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type Vertical / Horizontal 230/250V single phase 2000 watts 5 Star rated water heater with ABS plastic body of capacity to withstand up to 8.0 bar of water pressure including all standard accessories and dead weight pressure reducing valve on out let side, including cost of 2 Nos SS flexible braided hose pipe, testing and all labour charges etc., complete. Makes : Crompton / Jaquar / Venus / Racold / AO Smith / Havells / Bajaj or equivalent as approved by the Dept. | 1 | Nos | 1 | No | 12735 | 12735
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Run of 3 1.5 sq mm
117 | 24-25 RSD 3.1.4 |  | Supply of and run of 3 (1.5 Sqmm) FRLS / HFFR PVCinsulated 1100V grade as per IS:694/1990 specification for of Copper Cable Makes : Finolex / RR kabel / Havells / Polycab /Beljin (HFFR) /Ollvin(HFFR) / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million(HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (FRLS / HFFR) / Bonton (HFFR) and Avocab (HFFR) / Fortune Arrt (HFFR) / SPM (HFFR) / Sudhakar (HFFR) / Nakoda (HFFR) / HPL (HFFR) / GLOSTER (HFFR) / Rajnigandha (HFFR) / Pawancab (HFFR) / South King (HFFR).
Copper Cable Makes : Finolex / RR kabel / Polycab / Havells / KEI (HFFR) / L&T / V-Guard (HFFR).
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.67 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 2 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.67 | day | 1 | day | 615
Labour for 100 Mtr
Labour for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-1.5.1-b | 4 | Supply of and run of 3 (1.5 Sqmm) FRLS / HFFR PVCinsulated 1100V grade as per IS:694/1990 specification for of Copper Cable Makes : Finolex / RR kabel / Havells / Polycab /Beljin (HFFR) /Ollvin(HFFR) / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million(HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (FRLS / HFFR) / Bonton (HFFR) and Avocab (HFFR) / Fortune Arrt (HFFR) / SPM (HFFR) / Sudhakar (HFFR) / Nakoda (HFFR) / HPL (HFFR) / GLOSTER (HFFR) / Rajnigandha (HFFR) / Pawancab (HFFR) / South King (HFFR). | 300 | Mtrs | 100 | Mtrs | 2410
Cost of Material for 100 Metres
Cost of Material Rate per Mtr= C/100
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
19/20 mm PVC bends
118 | 24-25 RSD 2.1.6 |  | Supply of 19/20 mm dia Medium grade PVC Bends. Makes : Sudhakar / Finolex / Modi / VIP / Precision / DEC / Beljin
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.2.8.a | 6 |  | 1 | Nos | 1 | No | 8
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
20mm SWR Flexible Conduit Pipe
119 | 24-25 RSD 2.1.6 |  | Supply of 20mm SWR reinforced Flexible Conduit Pipe. Make: Precision or its equivalet as approved by the department
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 No
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.2.3 a | 6 |  | 1 | Nos | 1 | No | 18
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
6/10 2 Way switches
Data-120
120 | 24-25 RSD 2.1.4 |  | Supply and fixing of ISI Marked 6/10A 2 way Modular switch including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.b | 6 | Supply and fixing of ISI Marked 6/10A 2 way Modular switch including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 100
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
10A Modular Bell Push with Neon Indicator
Data-121
121 | 24-25 RSD 2.1.4 |  | Supply and fixing of ISI Marked 10A Modular Bell Push with Neon Indicator including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.f | 6 | Supply and fixing of ISI Marked 10A Modular Bell Push with Neon Indicator. including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 120
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
20A 2 Module Modular Socket with shutter
Data-122
122 | 24-25 RSD 2.1.4 |  | Supply and fixing of ISI Marked 20A 2 Module Modular Socket with shutter including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.02 | day | 1 | day | 735
|  | 2 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.01 | day | 1 | day | 615
Labour for 1 Point
Add GHMC allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.f | 6 | Supply and fixing of ISI Marked 20A 2 Module Modular Socket with shutter including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | No | 180
Total material cost
Total Material and Labour charges for 1 no
Add Overhead @ 10.615%
Total Rate
Rounded off rate
25 to 32A Modular type Motor Starter Switch
Data-123
123 | 24-25 RSD 9.7.26 |  | Supply and fixing of 25 to 32A Modular type Motor Starter Switch with connections and Labour charges etc complete. Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | Nos | 1 | Nos | 735
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC-1.9.2.n | 2 | Supply of 25 to 32A Modular type Motor Starter Switch of Makes : Legrand Lyncus / GM Four Five / Million / Goldmedal Curve / Anchor Roma Plus / Crabtree Verona / Panasonic Vision / Hager Insista / Benlo Vesta / Polycab Levana / Salzar Elite / Elleys E-Soft / Fybros Four-X | 1 | Nos | 1 | Nos | 615
Total material cost
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
WPTC 6 sq mm
Data-124
124 | 24-25 RSD 9.7.26 |  | Supply of 6 sq mm WPTC (Weather Proof Twin Core) ISI mark Alluminium Wire. Makes : Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Gemini / Vimal /Suncab / Stanjo / Rajnigandha / Orbit / Beljin / Pawancab
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.1 | Nos | 1 | Nos | 735
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC-1.6.2.a | 2 |  | 1 | RM | 100 | RM | 3920
Total material cost
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
Casing And Capping 25 mm
Data 125
125 | 24-25 RSD 1.3.2 |  | Supply of 25mm x 12 mm and thickness 1.2 mm width and height Casing and Caping with all accessories such as Ts, Bends, Elbows etc., complete for finished item of work. Makes : Modi with ISI or its equivalent make as approved by the department
Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC
|  |  | a) Labour charges : | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 1 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
Labour Rate Per 100 Rm
Labour Rate for 1 Mtr
Add GHMC Allowance @40%
Labour subtotal
b) Material
| Elec 10.1.2 | 4 | Rawl Plugs. (SOR-2024-25- ELEC-10.1.2) | 200 | Nos | 100 | Nos | 45
| Elec 1.4.4-d | 5 | Supply of No.8 Screws of 35/38mm. (SOR-2024-25 ELEC-1.4.4-d) | 200 | Nos | 100 | Nos | 135
| Elec 1.2.5 b | 10 |  | 100 | Mtr | 1 | Mtr | 32
Material Rate for 100 Mtrs
Material Rate for 1 Mtr
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
4P 63 A MCBs
Data 126
126 | 24-25 RSD 4.4.4A |  | Supply of 50-63A FP MCB kA, C/D Curve ISI Mark. Makes : Legrand-DX3 / Schneider-Acti9 /Siemens / LK (L&T) Exora / Crabtree / Indo Asian / BCH
DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
|  |  | a) Labour charges for Flush Mounting | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.033 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.02 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.02 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-2.13.1 -I | 8 |  | 1 | Nos | 1 | No | 3150
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
6 way VTPN DB
Data 127
127 | 24-25 RSD 4.4.2b |  | Supply of 6 Way VTPN DB with Protection as IP 43 per IS:13032 and suitable for accommodating T.P. / S.P. as out goings and 125A / 160A 4 pole MCCB as Incomer with 250 A tinned copper busbar, neutral bar, earth bar and cable ties for cable management, fully shrouded neutral bar, profile blanking modules for unused MCB ways, din bars and detachable gland plate etc complete with inter connections. Makes : Legrand / Schneider / Siemens / LK (L&T) / Hager / Crabtree Xpro / BCH
|  |  | LABOUR | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 4 | Semi Skilled Mason. SOR-2024-25 Sl No 35 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | day | 615
COST OF LABOUR for 1 no
Add GHMC Allowance @40%
Labour Sub total
MATERIAL
| ELEC-2.15.1-d | 6 |  | 1 | Nos | 1 | No | 17600
Cost of Material
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
8'' Exhaust Fan with Shutters
Data 128
128 | 24-25 RSD 9.7.2+RSD 9.7.36 |  | Supply of 8" (200mm) Ventilating exhaust fan with shutters etc complete Makes : Crompton / Havells Ventilair / Orient /Panasonic / Halonix
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.25 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.25 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
|  | 3 | Sundries such as Bolt, Nuts, twin core wire if necessary etc. |  |  |  |  | 15
Cost of Material for fixing fan
b) Material
| ELEC-5.1.14 b | 4 | Supply of 8" (200mm) Ventilating exhaust fan with shutters etc complete Makes : Crompton / Havells Ventilair / Orient /Panasonic / Halonix | 1 | No | 1 | No | 1805
|  |  | Transportation Charges on Unit Cost @1% |  |  |  |  | 1%
Cost of Material for 1 No
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
18 W LED Slimline Panel Light
Data-129
129 | SD-NA |  | Supply and transportation of 18 W +/-10% (>= 1800 Lumens) back lit LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI>80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE : Phillips / OSRAM / Wipro/ Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Eveready / Surya / Keselec / Arraystorm / GM / Goldmedal / Goldwyn / Fortune Arrt / Lighting Technologies LED MAKE : PHILIPS LUMILEDS / CREE /NICHIA / OSRAM / SAMSUNG / LG LEDs.
|  |  | a) Labour charges | Quantity |  | Unit |  | Rate | Amount
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.062 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.062 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.062 | day | 1 | No | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC- 3.3.7-c | 4 |  | 1 | no | 1 | no | 1500
|  | 5 | Alluminium Flat,screws / hooks,binding wire (As per requirement). | [5 empty] | 20
Cost of Material for fixing luminaire
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
1.5 HP Open well Submersible
Data-130
130 | SD-11.1.3 |  | Replacement of old damaged with new Supply, Transportation and Installation of 1.5 HP Single phase open well ISI submersible motor pumpset. Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon
a) Labour charges
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | No | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC- 5.5.1 d | 4 | Supply and Transportation of 1.5 HP 21 stage single phase ISI submersible motor pumpset suitable for 4" Bore well. Makes: Texmo / CRI / KSB / Aryenvarsha /Lubi / Falcon | 1 | no | 1 | no | 16000
Cost of Material
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
3 Core x 2.5 Sqmm Flat Copper Cable for Motors
Data 131
131 | Finished item |  | Repalcement and laying of 3 Core 2.5 sq mm Flat Copper cable of ISI for Submersible Motors. Makes : Finolex / RR Kabel / Havells / KEI / LK(L&T) / Pawancab
b) Material
| ELEC-1.6.3 b | 1 | Supply of 3 Core 2.5 sq mm Flat Copper cable of ISI for Submersible Motors. Makes : Finolex / RR Kabel / Havells / KEI / LK(L&T) / Pawancab | 100 | Mtrs | 1 | Mtrs | 12400
Cost of Material
| Provisional rate | 2 | Labour for laying | 1 | Mtrs | 1 | Mtrs | 6
Total Cost of Material + Labour Charges
4 passenger lift
Data-1
1 |  |  | Supply, transportation,installation and commissioning of 4 passenger hydraulic passenger elevator with following specifications including required accessories and with all civil works required for installation of lift at staircase area.Make:M/s.Celsius Systems | 1 | No | 1 | No | 134000 | 134000
1.Capacity: 300 Kgs(4 persons)
|  | 1 | 2.Type of Lift :Pearl Series(Hydraulic Home Elevator with Indian MS Shaft with 8 mm Indian Toughened Glass)
3.Power requirement : a) Main Supply: 415 V, Three phase 50Hz A.C duly earthed b) Aux. Supply: 230 V, Single phase A.C. duly earthed
4.Speed:0.3 Mts/Sec,
5.Travel distance : 3.5 Mts (G + 1 Floors)
6. Type of drive : Electronically controlled hydraulic drive
7.Location of Power Unit :Near the lift shaft in ground floor
8. Key Civil Dimensions of Lift Shaft : 900 (W) X 1270 (D) X 6560 (H) Bottom pit required: 150 mm min
9. Passenger Cabin Dimensions : 650 mm (W) X 855 mm (D) X 2000 mm (H)
10.Cabin Corner Profile: Anodized Aluminum Silver finish Back & Left Wall: 304 Hairline SS Finish Right Wall Laminated Toughened Transparent Glass Ceiling Designer Celling g 304 HLSS with LED & Ventilation Flooring: imported PVC or Raw with 18 mm recess.
11.Clear Door Opening: 600 mm (W) X 2000 mm (H)
12.Car Door Finish: Big Vision Transparent glass + 304 Hairline SS Finish Frame
13.Landing Door Finish:Big Vision Transparent glass + 304 Hairline SS Finish Frame
14.COP/LOP:304 Hairline SS finish surface plate Sliver button & Digital Display
15.Shaft Structure: Indian MS Shaft with 8 mm Indian Toughened Glass
Total Cost of Material
Rounded off rate
3 HP Borewell Pumpset
Data-1
1 |  |  | Replacement of star rated 3.00 HP 5-10 Stage Three phase ISI submersible motor pumpset suitable for 6" Bore well. Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon
a) Labour charges
|  |  | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.67 | day | 1 | day | 735
|  |  | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.67 | day | 1 | day | 615
|  |  | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.67 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-5.6.1.a | 2 | Supply ,transportation and fixing of star rated 3.00 HP 5-10 Stage Three phase ISI submersible motor pumpset suitable for 6" Bore well. Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon | 1 | No | 1 | No | 40000
Total material cost
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
3 HP Monoblock Pumpset
Data-2
2 |  |  | Repalcement of 3.00 HP Three phase Mono block IP44 motor pumpset Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon
a) Labour charges
|  |  | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.67 | day | 1 | day | 735
|  |  | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 0.67 | day | 1 | day | 615
|  |  | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.67 | day | 1 | day | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour subtotal
b) Material
| ELEC-5.9.6.b | 2 | Supply,transportation and fixing of 3.00 HP Three phase Mono block IP44 motor pumpset Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon | 1 | No | 1 | No | 36500
Total material cost
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
7.5 HP Monoblock Motor Pump Set
Data-1
1 | SD-11.1.3 |  | Replacement of old damaged by new Supply, Transportation and installation of 7.5 HP Mono block IP44 motor pumpset Three Phase (under buy back) Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon
a) Labour charges
|  | 1 | Skilled Electrician. SOR-2024-25 Sl No 5 of cat-I Skilled Labour rates. | 0.5 | day | 1 | day | 735
|  | 2 | Semi skilled Electrician / Helper. SOR-2024-25 Sl No 34 of cat-II Semi skilled Labour rates. | 1 | day | 1 | day | 615
|  | 3 | Helper. SOR-2024-25 Sl No 34 of Cat-II Semi skilled Labour rates. | 0.5 | day | 1 | No | 615
Labour for 1 No
Add GHMC Allowance @40%
Labour Sub total
b) Material
| ELEC- 5.9.6 d | 4 |  | 1 | no | 1 | no | 51200
| ELEC-16.1.1 o |  | Dismantled material All types of pumpsets under buy back | 1 | no | 1 | no
Cost of Material
Total Cost of Material + Labour Charges
Add Overhead @ 10.615%
Total Rate
Rounded off rate
END
Data-2
2 |  |  | Repalcement of 3.00 HP Three phase Mono block IP44 motor pumpset Makes: Texmo / CRI / KSB / Aryenvarsha / Lubi / Falcon
a) Labour charges

## Groups
Item Name | Group | Prefix
Concealed PVC Pipe | Piping | Replacement of old damaged u/s by new
Surface PVC Pipe | Piping | Replacement of old damaged u/s by new
Light & Bell Points in RB | Points | Re-
Fan and Exhaust Fan Points in RB | Points | Re-
Common Switch Board | Switch Boards | Replacement of old damaged u/s by new
Power Plug | Switch Boards | Replacement of old damaged u/s by new
Power Plug Two Nos | Switch Boards | Replacement of old damaged u/s by new
6Module (6A Sockets & -6A Switches - Two Nos) | Switch Boards | Replacement of old damaged u/s by new
12Module (6A Sockets & -6A Switches - Four Nos) | Switch Boards | Replacement of old damaged u/s by new
8 Module switch Board (6A Sockets & 6A Switches-3 Nos) | Switch Boards | Replacement of old damaged u/s by new
1200mm length LED light | Luminaire | Replacement of old damaged u/s by new
15W LED Slimline Panel Light | Luminaire | Replacement of old damaged u/s by new
36W 2' x2' (600mm x 600mm) slim panel LED | Luminaire | Replacement of old damaged u/s by new
Ceiling Fans | Fans | Replacement of old damaged u/s by new
Stepped Electronic Regulator | Fans | Replacement of old damaged u/s by new
Exhaust Fan | Fans | Replacement of old damaged u/s by new
Ding Dong Bell | Bells | Replacement of old damaged u/s by new
Musical Bell | Bells | Replacement of old damaged u/s by new
Run of 3 of 2.5 Sq.mm Copper Cable | Wiring and cables | Re-
Run of 3 of 4.0 Sq.mm Copper Cable | Wiring and cables | Re-
Run of 5 of 6.0 Sq.mm Copper Cable | Wiring and cables | Re-
4Way TPN DB | DBs | Replacement of old damaged u/s by new
8Way VTPN DB | DBs | Replacement of old damaged u/s by new
Water Heater (Geysers) | Water Heater | Replacement of old damaged u/s by new
Water Heater hose pipe | Water Heater | Replacement of old damaged u/s by new
Street Light | Luminaire | Replacement of old damaged u/s by new
Bollard | Luminaire | Replacement of old damaged u/s by new
3 Core x 2.5 Sqmm Armoured Cable | Wiring and cables | Replacement of old damaged u/s by new
Panel Board | Panels | Replacement of old damaged u/s by new
4way SPN DB | DBs | Replacement of old damaged u/s by new
8way SPN DB | DBs | Replacement of old damaged u/s by new
Run of 1 of 1.50 Sq.mm | Wiring and cables | Re-
70 Sqmm Cable | Wiring and cables | Re-
Laying of 70 Sqmm Cable | Wiring and cables | Re-
Earthwork excavation of UG Cable | Earthing
50 mm Nominal Bore GI pipe | Earthing | Replacement of old damaged u/s by
35 Sqmm Cable | Wiring and cables | Re-
25 Sqmm Cable | Wiring and cables | Re-
Laying of 35 & 25 Sqmm Cable | Wiring and cables
Speaker Cable | Mic System | Replacement of old damaged u/s by
4Module 3W LED Foot lamp | Luminaire | Replacement of old damaged u/s by
3W LED light passolite | Luminaire | Replacement of old damaged u/s by
LED Strip 28W | Luminaire | Replacement of old damaged u/s by
4 Way VTPN DB | DBs | Replacement of old damaged u/s by
Independent earthing | Earthing
8 SWG GI Wire | Earthing | Replacement of old damaged u/s by
12Way SPN DB | DBs | Replacement of old damaged u/s by
Heavy duty long barrel alluminium 70 sq mm lugs | Lugs | Replacement of old damaged u/s by
Heavy duty long barrel alluminium 35 sq mm lugs | Lugs | Replacement of old damaged u/s by
Heavy duty long barrel alluminium 16 sq mm lugs | Lugs | Replacement of old damaged u/s by
Mirror Lights | Luminaire | Replacement of old damaged u/s by
Telephone Cable | EPABX System | Replacement of old damaged u/s by
IP Based digtal Telephone | EPABX System | Replacement of old damaged u/s by
Digital Key Telephone with 2 line display | EPABX System | Replacement of old damaged u/s by
50pair Telephone distribution box | EPABX System | Replacement of old damaged u/s by
20 pair Telephone distribution box with back mount frame | EPABX System | Replacement of old damaged u/s by
Caller ID Pushbutton | EPABX System | Replacement of old damaged u/s by
2Port Line Protection | EPABX System | Replacement of old damaged u/s by
600 mm width x 500 mm net work rack | EPABX System | Replacement of old damaged u/s by
Modular telephone Jack with connector | EPABX System | Replacement of old damaged u/s by
LAN Cable cat - 6 UTP cable | LAN system | Re-
8 Port D-Link Desktop Switch | LAN system | Replacement of old damaged u/s by
3 feet length moulded patch cord | LAN system | Replacement of old damaged u/s by
Wireless-N300 Routewith RJ 45 Jacks | LAN system | Replacement of old damaged u/s by
600 mm width x 500 mm network Rack | LAN system | Replacement of old damaged u/s by
RG-6 Cu flexible cable | TV | Replacement of old damaged u/s by
Cat 6 RJ 45 Outlet | LAN system | Replacement of old damaged u/s by
TV Socket | TV | Replacement of old damaged u/s by
2.0/1.8 TR Split AC's | HVAC | Replacement of old damaged u/s by
1.5 TR Split AC's | HVAC | Replacement of old damaged u/s by
Copper Pipe | HVAC | Replacement of old damaged u/s by
3core 2.5 Sqmm | HVAC | Re-
CPVC Pipe | HVAC | Replacement of old damaged u/s by
Core Cutting | HVAC
1.00 HP Open Well Motor | Motor Pumpsets | Replacement of old damaged u/s by
Control Panel | Motor Pumpsets | Replacement of old damaged u/s by
25mm GI Pipe | Motor Pumpsets | Replacement of old damaged u/s by
25mm Gate Valve | Motor Pumpsets | Replacement of old damaged u/s by
3 Core 4.0 Sqmm Flat Copper Cable | Wiring and cables | Re-
Water Dispenser | Drinking Water Equipment | Replacement of old damaged u/s by
Water Purifier | Drinking Water Equipment | Replacement of old damaged u/s by
40 KVA DG Set | DG | Replacement of old damaged u/s by
125A 4 Pole Changeover | Changeovers | Replacement of old damaged u/s by
125A 4 Pole MCCB | Protection Equipment | Replacement of old damaged u/s by
Independent Copper earthing | Earthing
Independent GI earthing | Earthing
GI Strip | Earthing | Replacement of old damaged u/s by
Copper Strip | Earthing | Replacement of old damaged u/s by
4 Passeneger Lift | Elevators | Replacement of old damaged u/s by
20Pair Telephone Distribution Box | EPABX System | Replacement of old damaged u/s by
Modular Telephone Jack | EPABX System | Replacement of old damaged u/s by
LAN Cable CAT-6 UTP | LAN system | Re-
8 Port D-Link DGS-1008A 8-Port Gigabit Switch | LAN system | Replacement of old damaged u/s by
D-Link DIR-615 Wireless-N300 Router | LAN system | Replacement of old damaged u/s by
6U Wall mounting Rack | LAN system | Replacement of old damaged u/s by
Cat 6 RJ-45 information outlets | LAN system | Replacement of old damaged u/s by
Modular co-Axial socket type TV Antenna outlet | TV | Replacement of old damaged u/s by
LED Bulbs | Luminaire | Replacement of old damaged u/s by
Batten Holders | Holders | Replacement of old damaged u/s by
2Module boxes with cover frame | Switch Boards | Replacement of old damaged u/s by
3 Modular switch boards with cover frame | Switch Boards | Replacement of old damaged u/s by
4 Module boxes with cover frame | Switch Boards | Replacement of old damaged u/s by
6 Modular switch boards with cover frame | Switch Boards | Replacement of old damaged u/s by
8Module boxes with cover frame | Switch Boards | Replacement of old damaged u/s by
12 Module switch boards with cover frame | Switch Boards | Replacement of old damaged u/s by
18 Module boxes with cover frame | Switch Boards | Replacement of old damaged u/s by
10A 3/2 Pin 2 Module Modular Socket with shutter. | Switches and Sockets | Replacement of old damaged u/s by
16A sockets | Switches and Sockets | Replacement of old damaged u/s by
6/10 switches | Switches and Sockets | Replacement of old damaged u/s by
16/20 switches | Switches and Sockets | Replacement of old damaged u/s by
63A FP Isolators | Protection Equipment | Replacement of old damaged u/s by
6-32A MCBs | Protection Equipment | Replacement of old damaged u/s by
Water Geyser | Water Heater | Replacement of old damaged u/s by
Run of 3 1.5 sq mm | Wiring and cables | Re-
19/20 mm PVC bends | Piping | Replacement of old damaged u/s by
20mm SWR Flexible Conduit Pipe | Piping | Replacement of old damaged u/s by
6/10 2 Way switches | Switches and Sockets | Replacement of old damaged u/s by
10A Modular Bell Push with Neon Indicator | Switches and Sockets | Replacement of old damaged u/s by
20A 2 Module Modular Socket with shutter | Switches and Sockets | Replacement of old damaged u/s by
25 to 32A Modular type Motor Starter Switch | Switches and Sockets | Replacement of old damaged u/s by
WPTC 6 sq mm | Wiring and cables | Re-
Casing And Capping 25 mm | Piping | Replacement of old damaged u/s by
4P 63 A MCBs | Protection Equipment | Replacement of old damaged u/s by
6 way VTPN DB | DBs | Replacement of old damaged u/s by
8'' Exhaust Fan with Shutters | Fans | Replacement of old damaged u/s by
18 W LED Slimline Panel Light | Luminaire | Replacement of old damaged u/s by
1.5 HP Open well Submersible | Motor Pumpsets | Replacement of old damaged u/s by
3 Core x 2.5 Sqmm Flat Copper Cable for Motors | Motor Pumpsets | Replacement of old damaged u/s by
4 passenger lift | Elevators | Replacement of old damaged u/s by
3 HP Borewell Pumpset | Motor Pumpsets | Replacement of old damaged u/s by
3 HP Monoblock Pumpset | Motor Pumpsets | Replacement of old damaged u/s by
7.5 HP Monoblock Motor Pump Set | Motor Pumpsets | Replacement of old damaged u/s by
END